TECHNICAL SPECIFICATIONS

25KVA, SINGLE PHASE, SILENT TYPE GENERATOR SET FOR DBP VIGA BLU

ENGINE:

| - Rating | : | 25KVA |
| --- | --- | --- |
| - Engine Speed | : | 1800RPM |
| - No. of Cylinders (Bore/Stroke) | : | ≥ 4 (80mm / 90mm) |
| - Displacement | : | ≥ 1.2L |

FUEL SYSTEM:

| - Fuel Tank Capacity | : | ≥ 60L (Diesel) |
| --- | --- | --- |
| - Lube Oil Capacity | : | ≥ 4L |
| - Coolant Capacity | : | ≥ 6L |

BATTERY PARAMETERS:

| - Battery Capacity | : | ≥ 12V, 65AH |
| --- | --- | --- |
| - Battery Type | : | Lead Acid Battery with suspended Electrolyte or equivalent |

ALTERNATOR:

| - Output Rating | : | ≥ 25KVA (continuous/prime power) |
| --- | --- | --- |
| - Rated Voltage Range | : | 208 to 240V |
| - Frequency | : | 60Hz ±5% |
| - No. Of Phases | : | 1-Phase, 2-wire (L-N) + ground |
| - Power Factor | : | 0.8 (Lagging) |
| - Voltage regulation (%) | : | Within ± 1.5 |
| - Insulation type | : | ≥ Class H |
| - Energizer (Exciter) Type | : | Brushless, Rotating Energizer with Automatic Voltage Regulator |

CONTROL SYSTEM:

| - Automatic Controller | : | Integrating digital, programmable, network technology for automation and monitoring |
| --- | --- | --- |
| - Features | : | Implements an automatic starting / stopping, data measurements, & alarm protection function of the generator set. |
| - Accessories | : | Voltmeter, Ammeter, Frequency, Water temperature Gauge, Battery condition meter, Hours run meter, Mode selector (Auto, Run, Off), Set mounted MCCB, Cubicle for Genset |