## Sheet1
[114 empty] | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
GENERAL REQUIREMENTS | Construction health and safety program | lot | 0 | 10% | 10% | Maintenance of existing septic tank | lot | 15% | 10% | 25% | Formworks | lot | 15% | 10% | 25% | Stone cleaning/maintenance | lot | 15% | 10% | 25% | Rust-proofing | lot | 15% | 10% | 25% | Wood infestation removal | lot | 15% | 10% | 25% | Maintenance of dampproofing/waterproofing | lot | 15% | 10% | 25% | Solid wood door - 700mm width | set/s | 15% | 10% | 25% | Plaster and gypsum board - single wall | sqm | 15% | 10% | 25% | Horizontal façade signage | sqm | 15% | 10% | 25% | Lateral filing drawers (3 layer) | set/s | 0 | 10% | 10% | 25mm dia BI pipe (6m/pc) | pc/s | 15% | 10% | 25% | Water closet (tank type, push-button) | set/s | 15% | 10% | 25% | 1.0 HP single phase inverter split type air-conditioning system (wall mounted) | set/s | 15% | 10% | 25% | 5 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | Cat5e UTP cable 4 pairs for voice (305m/box) | box/es | 15% | 10% | 25% | Cat5e UTP cable 4 pairs (305m/box) | box/es | 15% | 10% | 25% | Soil for earthwork | cum | 15% | 10% | 25% | Paving cleaning | lot | 15% | 10% | 25% | Backhoes | lot | 15% | 10% | 25% | a.) Wearing of ANSI standard PPEs, provision of safety signages and compliance to DOH, DOLE and LGU protocols shall be observed on the project site. b.) A bonafide Safety Officer shall always be present on site. |  | Maximum re-use of formworks shall be: 7 uses/repetition for 12mm thick plywood and 20 for uses/repetition for 18mm thick plywood | [5 empty] | a.) Partition materials shall be made of 12.5mm thick gypsum board (one side only) on GA#20 metal studs spaced at 0.60m both ways. b.) Verify actual height and location of wall on architectural plans. | a.) Signage material shall be made of ACP with matte spray painted DBP colors including painted aluminum casing and embossed illuminated DBP logo with timer. b.) Signage casing shall be made of 1” x ½” x 1.5mm tubular framing. c.) DBP Logo shall be acrylic plastic, embossed, white in color and lighted from inside. d.) Contractor shall tap the signage to the power supply. e.) Framing per using 2" x 2" tubular steel (separate item) f.) Refer to signage details. | a.) Drawer shall be Three (3) layes, cold-rolled steel plate, gauge #20, packed with polyfoam inner lining and multi-layer. b.) Drawer dimensions: 900mm length x 450mm width x 1060mm height. c.) Finish shall be durable epoxy powder and powder coating finished. d.) Central lock mechanism shall be included. e.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Prefered water closed dimensions: 732mm height x720mm length x 393mm width or equivalent b.) Water closet shall be tank-type, 6LPF with single push-button flush, close coupled, elongated and with semi-concealed full glazed trap way. c.) Finish shall be made of fully glazed and polished white ceramic. d.) All necessary accessories in order to operate the water closet shall be included. e.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 10kVA 60hz 230V single phase generator set (portable) | lot | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor shall ensure it does not contain "controlled refrigerants". c.) Contractor to install necessary accessories: AC refrigerant, refrigerant pipes & fittings, insulation, drain pipe, hanger & support d.) Contractor must submit sample/s, technical specificication for DBP's approval before installation. | a.) Capacity: 5kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pad/Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | a.) Cat5e UTP cable 4 pairs min. 100mbps receiving b.) Conductors: Solid bare copper conductors c.) Insulators: Polyolefin insulation d.) Jacket: Gray PVC jacket with rip cord | a.) Cat5e UTP cable 4 pairs min. 100mbps receiving b.) Conductors: Solid bare copper conductors c.) Insulators: Polyolefin insulation d.) Jacket: Gray PVC jacket with rip cord | 1.) ENGINE a.) Rating: 10KVA b.) Operating Voltage range: 208 to 240V c.) Frequency: 60Hz ±5% d.) Engine speed: ≥ 1500 RPM e.) Governor type: Electrical f.) No. of Cylinders: ≥ 2 g.) Compression ratio: 9.5:1 / 17.5:1 / 19:1 h.) Bore: 80 to 92mm i) Stroke: 82.4 to110mm j.) Displacement: 1.3 to 2L k.) Lubrication oil 2.) FUEL SYSTEM a.) Fuel system: Diesel b.) Fuel Tank capacity: 50 to 70L c.) liquid cooling 3.) BATTERY PARAMETERS a.) Battery voltage: 12V,68Ah b.) Battery type: Lead Acid Battery with suspended, Electrolyte c.) Starting Voltage: 12v DC in parallel 4.) ALTERNATOR a.) 10KVA output rating b.) Operating Voltage range: 208 to 240V c.) Frequency: 60Hz ±5% d.) 1-phase, 2-wire + ground e.) 0.8 (lagging) power factor f.) ±0.5 within voltage regulation g.) Insulation type: class H h.) Energizer Type: Brushless, self-energized 5.) CONTROL SYSTEM a.) Automatic controller shall be integrating digital, intelligent, network technology uses for a single diesel generator set for automation & monitoring. b.) Implements an automatic starting / stopping, data measurements, and alarm protection function of the generator set. c.) Voltmeter, Ammeter, Frequency, Water temperature gauge, Battery condition meter, Hours run meter, Mode selector (Auto, Run, Off), Set mounted circuit breaker cubicle contained in a suitable rated molded case circuit breaker for the generator set.
SITE CONDITIONS | Security | lot | 0 | 10% | 10% | Shoring and support of existing structure | lot | 15% | 10% | 25% | Concrete on slab (on-grade) | cu.m | 15% | 10% | 25% | Stone restoration | lot | 15% | 10% | 25% | Rust removal | lot | 15% | 10% | 25% | Wood treatment/preservation | lot | 15% | 10% | 25% | Waterproofing replacement | sqm | 15% | 10% | 25% | Solid wood door - 800mm width | set/s | 15% | 10% | 25% | Plaster and gypsum board - double wall | sqm | 15% | 10% | 25% | Flag type signage | lot | 15% | 10% | 25% | Vertical filing cabinets | set/s | 0 | 10% | 10% | 32mm dia BI pipe (6m/pc) | pc/s | 15% | 10% | 25% | Water closet (tank type, lever type) | set/s | 15% | 10% | 25% | 1.5 HP single phase inverter split type air-conditioning system (wall mounted) | set/s | 15% | 10% | 25% | 10 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | Cat5e UTP cable 25 pairs for data and voice | lm | 15% | 10% | 25% | 25mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | Clearing and grubbing | sqm | 15% | 10% | 25% | Paving removal | lot | 15% | 10% | 25% | Bulldozers | lot | 15% | 10% | 25% | - |  | Concrete mixture/ratio shall be class B. |  |  | All wood components shall be treated with odorless and colorless wood preservative before using and finishing. |  |  | a.) Partition materials shall be made of 12.5mm thick gypsum board (double sided) on GA#20 metal studs spaced at 0.60m both ways. b.) Verify actual height and location of wall on architectural plans. | a.) Top signage dimensions: 1.5m length x 1.5m width x 0.2m thick b.) Bottom signage: 1.5m length x 0.45m width x 0.2m thick c.) Signage shall be double face illuminated signage using flexible substrate with translucent sticker and painted aluminum casing, complete with LED lighting fixture and timer. d.) Signage Casing: Lift-Up Type, 1”x ½” x 1.5mm tubular framing with painted aluminum sidings e.) Metal post and reinforced concrete pedestal shall be included. f.) Signage design and other details: refer to signage details |  |  | a.) Prefered water closed dimensions: 732mm height x720mm length x 393mm width or equivalent b.) Water closet shall be tank-type, 6LPF with lever flush, close coupled, elongated and with semi-concealed full glazed trap way. c.) Finish shall be made of fully glazed and polished white ceramic. d.) All necessary accessories in order to operate the water closet shall be included. e.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 15kVA 60hz 230V single phase generator set (outdoor type) | lot | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor shall ensure it does not contain "controlled refrigerants". c.) Contractor to install necessary accessories: AC refrigerant, refrigerant pipes & fittings, insulation, drain pipe, hanger & support d.) Contractor must submit sample/s, technical specificication for DBP's approval before installation. | a.) Capacity: 10kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | a.) Cat5e UTP cable 25 pairs min. 100mbps receiving b.) Conductors: Solid bare copper conductors c.) Insulators: Polyolefin insulation d.) Jacket: Gray PVC jacket with rip cord | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness, compression and impact resistant, non-corrosive, weatherproof
CONCRETE | Clearances/permit requirements | lot | 0 | 0 | 0 | Removal of existing soil erosion protection | lot | 15% | 10% | 25% | Concrete on slab (elevated) | cu.m | 15% | 10% | 25% | Stone cladding | sqm | 15% | 10% | 25% | Metal restoration | lot | 15% | 10% | 25% | Wooden trusses | bd.ft | 15% | 10% | 25% | Maintenance of membrane roofing | lot | 15% | 10% | 25% | Solid wood door - 900mm width | set/s | 15% | 10% | 25% | Cement plaster finish | sqm | 15% | 10% | 25% | ATM signage | sqm | 15% | 10% | 25% | Mobile pedestals | set/s | 0 | 10% | 10% | Fittings | lot | 15% | 10% | 25% | Water closet (tankless type, touchless) | set/s | 15% | 10% | 25% | 2.0 HP single phase inverter split type air-conditioning system (wall mounted) | set/s | 15% | 10% | 25% | 15 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | Cat6 UTP cable 4 pairs for (305m/box) | box/es | 15% | 10% | 25% | 25mm dia PVC elbow | pc/s | 15% | 10% | 25% | Tree and shrub removal | sqm | 15% | 10% | 25% | Mowing | lot | 15% | 10% | 25% | Compactors | lot | 15% | 10% | 25% | a.) Contractor shall assist in the application/processing of all necessary local clearances/permits including ECC/CNC for grounds-up project; and CoC and PTO for new generator set. b.) All plans and specifications shall be signed and sealed. c.) Reproduction of plans (11 sets) shall be included. d.) Approved copies of the documents and original receipts shall be turned-over to DBP. |  | Concrete mixture/ratio shall be class A. | [7 empty] | a.) Material shall be steel/metal (GA #22), oven baked in light gray enamel or powder coated finish. b.) Mobile pedestal shall include three (3) drawers with central locking mechanism, pencil tray, dividers, and ball casters for mobility. c.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Prefered water closed dimensions: 732mm height x720mm length x 393mm width or equivalent b.) Water closet shall be tankless with automatic sensor, close coupled, elongated and with semi-concealed full glazed trap way. c.) Finish shall be made of fully glazed and polished white ceramic. d.) All necessary accessories in order to operate the water closet shall be included. e.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 25kVA 60hz 230V single phase generator set (outdoor type) | lot | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor shall ensure it does not contain "controlled refrigerants". c.) Contractor to install necessary accessories: AC refrigerant, refrigerant pipes & fittings, insulation, drain pipe, hanger & support d.) Contractor must submit sample/s, technical specificication for DBP's approval before installation. | a.) Capacity: 15kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | a.) Cat6 UTP cable 4 pairs min. 100mbps receiving b.) Conduction: Solid bare copper conductors c.) Center member: Patented E-spline d.) Insulation: Polyolefin insulation | Elbow shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
MASONRY | Utility service connection (electrical) | lot | 0 | 0 | 0 | Demolition works | lot | 15% | 10% | 25% | Concrete on vault slab (elevated) | cu.m | 15% | 10% | 25% | CHB wall - 4" (masonry wall) | sqm | 15% | 10% | 25% | Steel trusses | kg | 15% | 10% | 25% | Wooden purlins | bd.ft | 15% | 10% | 25% | Roof removal | lot | 15% | 10% | 25% | Flush hollow core door - 700mm width (single) | set/s | 15% | 10% | 25% | Veneer finish | sqm | 15% | 10% | 25% | Pylon signage | sqm | 15% | 10% | 25% | Signature card cabinet | set/s | 0 | 10% | 10% | Consumables | lot | 0% | 10% | 10% | Lavatory (basin type) | set/s | 15% | 10% | 25% | 2.5 HP single phase inverter split type air-conditioning system (wall mounted) | set/s | 15% | 10% | 25% | 25 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | Cat6 UTP cable 25 pairs | lm | 15% | 10% | 25% | 25mm dia PVC coupling | pc/s | 15% | 10% | 25% | Tree and shrub trimming | lot | 15% | 10% | 25% | Pruning | lot | 15% | 10% | 25% | Excavators | lot | 15% | 10% | 25% | - | Refer to demolition plan | Concrete mixture/ratio shall be class A. | a.) CHB shall be 400 PSI compressive strength (minimum), normal in weight and in conformance to ASTM C-90, Type 1. b.) Rebar diameter shall be 10mm. c.) Concrete filler mixture/ratio shall be class A. d.) Both sides shall be plastered e.) Refer to CHB wall details at DBP standard booklet. | [6 empty] | a.) Cabinet dimensions: 1041.4mm length x 457.2mm width x 1358.9mm height b.) No of drawers: Twenty-one (21) c.) Cabinet shall be made of GA#20 steel component in light gray powder coated finish; with central lock mechanism and wheel casters. d.) Design shall be same or similar as to the photo at DBP standard booklet. | [10 empty] | 45kVA 60hz 230V single phase generator set (outdoor type) | lot | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor shall ensure it does not contain "controlled refrigerants". c.) Contractor to install necessary accessories: AC refrigerant, refrigerant pipes & fittings, insulation, drain pipe, hanger & support d.) Contractor must submit sample/s, technical specificication for DBP's approval before installation. | a.) Capacity: 25kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | a.) Cat6 UTP cable 4 pairs min. 100mbps receiving b.) Conduction: Solid bare copper conductors c.) Center member: Patented E-spline d.) Insulation: Polyolefin insulation | Coupling shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
METALS | Utility service connection (water) | lot | 0 | 0 | 0 | Salvage/relocation of existing materials | lot | 15% | 10% | 25% | Concrete on column | cu.m | 15% | 10% | 25% | CHB wall - 5" (masonry wall) | sqm | 15% | 10% | 25% | Steel purlins | kg | 15% | 10% | 25% | Wooden columns | bd.ft | 15% | 10% | 25% | Roof re-coating | sqm | 15% | 10% | 25% | Flush hollow core door - 800mm width (single) | set/s | 15% | 10% | 25% | Polished homogenous tile finish - beige (walls) | sqm | 15% | 10% | 25% | DBP logo (exterior) | set/s | 15% | 10% | 25% | Round table (0.90m dia) | set/s | 0 | 10% | 10% | Hangers and support | lot | 15% | 10% | 25% | Lavatory (wall-mounted type) | set/s | 15% | 10% | 25% | 3.0 HP single phase inverter split type air-conditioning system (wall mounted) | set/s | 15% | 10% | 25% | 37.5 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | Cat6 UTP patch cord 4 pairs (1 meter) | set/s | 15% | 10% | 25% | 25mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | Soil stockpiling | lot | 15% | 10% | 25% | Fertilizing and watering | lot | 15% | 10% | 25% | Graders | lot | 15% | 10% | 25% | - |  | Concrete mixture/ratio shall be class A. | a.) CHB shall be 400 PSI compressive strength (minimum), normal in weight and in conformance to ASTM C-90, Type 1. b.) Rebar diameter shall be 10mm. c.) Concrete filler mixture/ratio shall be class A. d.) Both sides shall be plastered e.) Refer to CHB wall details at DBP standard booklet. |  |  |  |  | a.) Tile size: 600mm x 600mm (verify applicable thickness) b.) Tiles shall be polished homogenous tiles (full body porcelain tiles) with beige finish. c.) 3mm tile grout matching the tile color shall be provided. d.) Contractor shall provide samples for DBP approval. e.) Refer to toilet elevations at architectural plans. | a.) Signage materials shall be embossed built-up acrylic diffuser illuminated with LED lighting fixture. b.) Acrylic diffuser shall be white in color. c.) LED lighting shall be installed and distributed evenly. d.) Contractor shall tap the signage to the power supply. e.) Framing per manufacturer's standard (separate item). f.) Refer to signage details. | a.) Table diameter: 0.90m b.) Table shall be made of 30mm thick MDF countertop in light gray high pressure laminate (HPL) finish with PVC edging and steel frame leg (hairline finish). c.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Prefered lavatory dimensions: 500mm length x 375mm width x 459mm thickness or equivalent b.) Lavatory shall be wall-mounted type and made of glazed and polished white ceramic finish. c.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 50kVA 60hz 230V single phase generator set (outdoor type) | lot | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor shall ensure it does not contain "controlled refrigerants". c.) Contractor to install necessary accessories: AC refrigerant, refrigerant pipes & fittings, insulation, drain pipe, hanger & support d.) Contractor must submit sample/s, technical specificication for DBP's approval before installation. | a.) Capacity: 37.5kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | a.) Cat6 UTP cable 4 pairs min. 100mbps receiving b.) Conduction: Solid bare copper conductors c.) Center member: Patented E-spline d.) Insulation: Polyolefin insulation | Adapter and locknut shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | 1.) ENGINE a.) Rating: 50KVA b.) Engine speed: ≥1500RPM c.) No. of cylinders (Bore/Stroke): ≥4 (80mm/90mm) d.) Displacement: ≥ 1.2L 2.) FUEL SYSTEM a.) Fuel tank capacity: ≥ 60L (Diesel) b.) Lube oil capacity & Coolant Capacity: ≥ 4L, and ≥ 6L 3.) BATTERY PARAMETERS a.) Battery type: ≥ 12V, 65Ah (Lead Acid Battery with suspended, Electrolyte or equivalent) 4.) ALTERNATOR a.) Output rating: ≥50KVA (continuous/prime power) b.) Operating Voltage range: 208 to 240V / 330 to 440V c.) Frequency and Power factor: 60Hz ±5%, 0.8 (lagging) d.) No. of phases: 1-phase, 2-wire + ground f.) Voltage regulation: within ±1.5 g.) Insulation type: class H h.) Energizer type: Brushless, rotating energizer with automatic voltage regulator 5.) CONTROL SYSTEM a.) Automatic controller: Integrating digital, programmable network technology for automation & monitoring. b.) Features: Implements an automatic starting / stopping, data measurements, and alarm protection function of the generator set. c.) Accessories: Voltmeter, Ammeter, Frequency, Water temperature gauge, Battery condition meter, Hours run meter, Mode selector (Auto, Run, Off), Set mounted MCCB cubicle for the Genset.
WOODS PLASTICS AND COMPOSITES | Temporary facilities | lot | 0 | 10% | 10% | Grinding of existing finishes | lot | 15% | 10% | 25% | Concrete on stiffener column | cu.m | 15% | 10% | 25% | CHB wall - 6" (masonry wall) | sqm | 15% | 10% | 25% | Steel columns | kg | 15% | 10% | 25% | Wooden beams | bd.ft | 15% | 10% | 25% | Roof replacement (verify specs on actual site) | sqm | 15% | 10% | 25% | Flush hollow core door - 900mm width (single) | set/s | 15% | 10% | 25% | Fabric-wrapped finish (walls) | sqm | 15% | 10% | 25% | DBP logo (interior) | set/s | 15% | 10% | 25% | Round table (1.00m dia) | set/s | 0 | 10% | 10% | Pendant type sprinkler heads | pc/s | 15% | 10% | 25% | Lavatory (under-counter type) | set/s | 15% | 10% | 25% | 4.0 HP/3 TR single phase inverter split type air-conditioning system (free standing) | set/s | 15% | 10% | 25% | 50 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | Cat6 UTP patch cord 4 pairs (3 meters) | set/s | 15% | 10% | 25% | 25mm dia PVC end bell | pc/s | 15% | 10% | 25% | Soil grading | lot | 15% | 10% | 25% | Soil sub-grade course | cum | 15% | 10% | 25% | Payloaders | lot | 15% | 10% | 25% | - | All existing walls, floor and concrete membranes shall be smooth and grinded prior to painting works. | Concrete mixture/ratio shall be class A. | a.) CHB shall be 400 PSI compressive strength (minimum), normal in weight and in conformance to ASTM C-90, Type 1. b.) Rebar diameter shall be 10mm. c.) Concrete filler mixture/ratio shall be class A. d.) Both sides shall be plastered e.) Refer to CHB wall details at DBP standard booklet. | [5 empty] | a.) Signage materials shall be acrylic diffuser with translucent sticker, built-up letters, logo and illuminated with LED lighting fixture. b.) Acrylic diffuser shall be white in color. c.) Translucent sticker shall be wet type, colors for background are 3630-157 Sultan blue and 3630-73 Dark red. d.) DBP text shall be 50mm thick built-up acrylic white diffuser. d.) DBP logo finish shall be 50mm thick polished stainless steel. e.) LED lighting shall be installed and distributed evenly. f.) Contractor shall tap the signage to the power supply. | a.) Table diameter: 1.00m b.) Table shall be made of 30mm thick MDF countertop in light gray high pressure laminate (HPL) finish with PVC edging and steel frame leg (hairline finish). c.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Prefered lavatory dimensions: 595mm length x 420mm width x 225mm thickness or equivalent b.) Lavatory shall be wall-under-counter type and made of glazed and polished white ceramic finish. c.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 25kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor shall ensure it does not contain "controlled refrigerants". c.) Contractor to install necessary accessories: AC refrigerant, refrigerant pipes & fittings, insulation, drain pipe, hanger & support d.) Contractor must submit sample/s, technical specificication for DBP's approval before installation. | a.) Capacity: 50kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | a.) Cat6 UTP cable 4 pairs min. 100mbps receiving b.) Conduction: Solid bare copper conductors c.) Center member: Patented E-spline d.) Insulation: Polyolefin insulation | End bell shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
THERMAL AND MOISTURE PROTECTION | Temporary utilities | lot | 15% | 10% | 25% | Chipping works | lot | 15% | 10% | 25% | Concrete on vault column | cu.m | 15% | 10% | 25% | CHB wall - 6" (vault wall) | sqm | 15% | 10% | 25% | Steel beams | kg | 15% | 10% | 25% | Wooden girders | bd.ft | 15% | 10% | 25% | Roofing restoration | lot | 15% | 10% | 25% | Flush hollow core door with louver - 700mm width | set/s | 15% | 10% | 25% | Laminated vinyl finish - legno fineline (walls) | sqm | 15% | 10% | 25% | Interior signages/decals | lot | 15% | 10% | 25% | Round table (1.20m dia) | set/s | 0 | 10% | 10% | Upright type sprinkler heads | pc/s | 15% | 10% | 25% | Urinal (push-button type) | set/s | 15% | 10% | 25% | 4.0 HP/3 TR three phase inverter split type air-conditioning system (free standing) | set/s | 15% | 10% | 25% | 75 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | AWG 22/25pairs alpeth cable | lm | 15% | 10% | 25% | 25.4mm dia IMC conduit (3m/pc) | pc/s | 15% | 10% | 25% | Excavation (structural) | cum | 15% | 10% | 25% | Aggregate Sub-base course | cum | 15% | 10% | 25% | Cement mixer trucks | lot | 15% | 10% | 25% | All utility consumption (water and power) during construction shall be charged to the Contractor. | Chipping of the following floor and wall potions: 1. Tile finishes 2. Provision of embedded conduits | Concrete mixture/ratio shall be class A. | a.) CHB shall be 700 PSI compressive strength (minimum) provided with test results, normal in weight and in conformance to ASTM C-90, Type 1. b.) Rebar diameter shall be 10mm. c.) Concrete filler mixture/ratio shall be class A. d.) Both sides shall be plastered e.) Refer to CHB wall details at DBP standard booklet. |  |  |  | a.) Door dimensions: 700mm width x 2100mm length/height x 44.5mm thickness. b.) Materials shall be 6mm thick marine plywood on both sides (flush hollow core), with kiln-dried tanguile framing and 400mm x 700mm wood louver panel. c.) Door jamb shall be 4" in thickness using solid kiln dried tanguile wood e.) Refer to schedule of doors at DBP standard booklet. | a.) Materials shall be laminated vinyl finish legno fineline finish on 6mm thick MDF board backing. b.) Contractor shall provide sample/s for DBP approval. c.) Refer to elevations at architectural plans. |  | a.) Table diameter: 1.20m b.) Table shall be made of 30mm thick MDF countertop in light gray high pressure laminate (HPL) finish with PVC edging and steel frame leg (hairline finish). c.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Prefered urinal dimensions: 740mm length x 480mm width x 300mm thickness or equivalent b.) Urinal shall be wall-mounted type with back inlet, push button flush, spreader and built-in p-trap. c.) Finish shall be made of fully glazed and polished white ceramic. d.) Urinal lower portion shall be 540mm above finish floor line. e.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 45kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor shall ensure it does not contain "controlled refrigerants". c.) Contractor to install necessary accessories: AC refrigerant, refrigerant pipes & fittings, insulation, drain pipe, hanger & support d.) Contractor must submit sample/s, technical specificication for DBP's approval before installation. | a.) Capacity: 75kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Alpeth cable 25 pairs min. 100mbps receiving | Conduits shall be hot-dip galvanized steel material and standard product length shall be 3.05m with coupling on one end
DOORS AND WINDOWS | Temporary scaffoldings and platforms | lot | 15% | 10% | 25% | Cleaning of existing toilet and/or pantry fixtures | lot | 15% | 10% | 25% | Concrete on column footing | cu.m | 15% | 10% | 25% | Solid concrete blocks | sqm | 15% | 10% | 25% | Steel girders | kg | 15% | 10% | 25% | Wooden joists (floor) | bd.ft | 15% | 10% | 25% | Roof accessories replacement | lot | 15% | 10% | 25% | Flush hollow core door with louver - 800mm width | set/s | 15% | 10% | 25% | Mood board | sqm | 15% | 10% | 25% | Main glass door decals | lot | 15% | 10% | 25% | Conference table | set/s | 0 | 10% | 10% | Isolation and draining of sprinkler system | lot | 15% | 10% | 25% | Urinal (lever type) | set/s | 15% | 10% | 25% | 5.0 HP/5 TR three phase inverter split type air-conditioning system (free standing) | set/s | 15% | 10% | 25% | 100 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 3.5mm sq. THHN stranded (150m/roll) | roll/s | 15% | 10% | 25% | 25.4mm dia IMC elbow | pc/s | 15% | 10% | 25% | Excavation (septic vault) | cum | 15% | 10% | 25% | Aggregate base-course | cum | 15% | 10% | 25% | Dump trucks | lot | 15% | 10% | 25% | - |  | Concrete mixture/ratio shall be class A. |  |  |  |  | a.) Door dimensions: 800mm width x 2100mm length/height x 44.5mm thickness. b.) Materials shall be 6mm thick marine plywood on both sides (flush hollow core), with kiln-dried tanguile framing and 400mm x 700mm wood louver panel. c.) Door jamb shall be 4" in thickness using solid kiln dried tanguile wood e.) Refer to schedule of doors at DBP standard booklet. | a.) Materials shall be matte finish vinyl sticker (verify design) on 6mm dent-resistant sintra board backing. b.) Refer to section at architectural plans. | a.) Decals shall be computer cut-out and wet-type installation. b.) Refer to decals details. | a.) Table dimensions for verification with DBP b.) Table shall be made of 30mm thick MDF countertop in light gray high pressure laminate (HPL) finish with PVC edging and steel frame leg. c.) Provide sample brochure with specifications for DBP approval. |  | a.) Prefered urinal dimensions: 740mm length x 480mm width x 300mm thickness or equivalent b.) Urinal shall be wall-mounted type with back inlet, lever flush, spreader and built-in p-trap. c.) Finish shall be made of fully glazed and polished white ceramic. d.) Urinal lower portion shall be 540mm above finish floor line. e.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 50kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor shall ensure it does not contain "controlled refrigerants". c.) Contractor to install necessary accessories: AC refrigerant, refrigerant pipes & fittings, insulation, drain pipe, hanger & support d.) Contractor must submit sample/s, technical specificication for DBP's approval before installation. | a.) Capacity: 100kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity | Elbow shall be hot-dip galvanized steel material. | 1.) ENGINE a.) Rating: 50KVA b.) Engine speed: ≥1500RPM c.) No. of cylinders (Bore/Stroke): ≥4 (80mm/90mm) d.) Displacement: ≥ 1.2L 2.) FUEL SYSTEM a.) Fuel tank capacity: ≥ 60L (Diesel) b.) Lube oil capacity & Coolant Capacity: ≥ 4L, and ≥ 6L 3.) BATTERY PARAMETERS a.) Battery type: ≥ 12V, 65Ah (Lead Acid Battery with suspended, Electrolyte or equivalent) 4.) ALTERNATOR a.) Output rating: ≥50KVA (continuous/prime power) b.) Operating Voltage range: 208 to 240V / 330 to 440V c.) Frequency and Power factor: 60Hz ±5%, 0.8 (lagging) d.) No. of phases: 3-phase, 3-wire + ground f.) Voltage regulation: within ±1.5 g.) Insulation type: class H h.) Energizer type: Brushless, rotating energizer with automatic voltage regulator 5.) CONTROL SYSTEM a.) Automatic controller: Integrating digital, programmable network technology for automation & monitoring. b.) Features: Implements an automatic starting / stopping, data measurements, and alarm protection function of the generator set. c.) Accessories: Voltmeter, Ammeter, Frequency, Water temperature gauge, Battery condition meter, Hours run meter, Mode selector (Auto, Run, Off), Set mounted MCCB cubicle for the Genset.
FINISHES | Temporary storage | lot | 15% | 10% | 25% | Cleaning of existing glasswall | lot | 15% | 10% | 25% | Concrete on wall footing | cu.m | 15% | 10% | 25% | Precast concrete blocks | sqm | 15% | 10% | 25% | Steel joists (floor) | kg | 15% | 10% | 25% | Wooden joists (ceiling) | bd.ft | 15% | 10% | 25% | Roof accessories restoration | lot | 15% | 10% | 25% | Flush hollow core door with louver - 900mm width | set/s | 15% | 10% | 25% | Sticker wall on sintra board backing | sqm | 15% | 10% | 25% | ATM cover (moveable) | set/s | 15% | 10% | 25% | Pentagon-type modular workstation (Cashier/BSO) | set/s | 0 | 10% | 10% | Selective dismantling of existing sprinkler system | lot | 15% | 10% | 25% | Urinal (automatic) | set/s | 15% | 10% | 25% | Drain pump | set/s | 15% | 10% | 25% | 150 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 5.5mm sq. THHN stranded (150m/roll) | roll/s | 15% | 10% | 25% | 25.4mm dia IMC coupling | pc/s | 15% | 10% | 25% | Trenching (drainage system) | cum | 15% | 10% | 25% | Asphalt paving | cum | 15% | 10% | 25% | Forklift trucks | lot | 15% | 10% | 25% | - |  | Concrete mixture/ratio shall be class A. |  |  |  |  | a.) Door dimensions: 900mm width x 2100mm length/height x 44.5mm thickness. b.) Materials shall be 6mm thick marine plywood on both sides (flush hollow core), with kiln-dried tanguile framing and 400mm x 700mm wood louver panel. c.) Door jamb shall be 4" in thickness using solid kiln dried tanguile wood e.) Refer to schedule of doors at DBP standard booklet. | a.) Materials shall be matte finish vinyl sticker (color: sultan blue) on 6mm dent-resistant sintra board backing b.) Refer to section at architectural plans. | a.) ATM cover shall be made of ACP panels with photo print sticker on 1" x 1" aluminum tubular frames including caster wheels. b.) Background sticker color shall be sultan blue. c.) Contractor shall veify actual measurements of ATM prior to fabrication of cover. d.) Refer to fabrication details. | a.) Countertop shall be 25mm thick MDF countertop in light gray high pressure laminate (HPL) finish with color matching PVC edging including 75mm diameter grommet holes. b.) Main countertop dimensions: 2000mm x 1800mm c.) Partition shall be tile-looked system with interlocking gauge #22 steel panel separated by an impregnated honeycomb paper core. Thickness shall be 50mm and trimming shall be aluminum alloy in powder-coated finish color gray. d.) Finish shall be blue fabric. e.) Panel raceway shall be hollow for telephone and electrical lines. Provide convenience outlet hole. f.) PVC keyboard tray shall be included. g.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Prefered urinal dimensions: 740mm length x 480mm width x 300mm thickness or equivalent b.) Urinal shall be wall-mounted type with back inlet, automatic flush sensor, spreader and built-in p-trap. c.) Finish shall be made of fully glazed and polished white ceramic. d.) Urinal lower portion shall be 540mm above finish floor line. e.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 63kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 150kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity | Coupling and connector shall be hot-dip galvanized steel material. | 1.) ENGINE a.) Rating: 63KVA b.) Engine speed: ≥1500RPM c.) No. of cylinders (Bore/Stroke): ≥4 (80mm/90mm) d.) Displacement: ≥ 1.2L 2.) FUEL SYSTEM a.) Fuel tank capacity: ≥ 60L (Diesel) b.) Lube oil capacity & Coolant Capacity: ≥ 4L, and ≥ 6L 3.) BATTERY PARAMETERS a.) Battery type: ≥ 12V, 65Ah (Lead Acid Battery with suspended, Electrolyte or equivalent) 4.) ALTERNATOR a.) Output rating: ≥63KVA (continuous/prime power) b.) Operating Voltage range: 208 to 240V / 330 to 440V c.) Frequency and Power factor: 60Hz ±5%, 0.8 (lagging) d.) No. of phases: 3-phase, 3-wire + ground f.) Voltage regulation: within ±1.5 g.) Insulation type: class H h.) Energizer type: Brushless, rotating energizer with automatic voltage regulator 5.) CONTROL SYSTEM a.) Automatic controller: Integrating digital, programmable network technology for automation & monitoring. b.) Features: Implements an automatic starting / stopping, data measurements, and alarm protection function of the generator set. c.) Accessories: Voltmeter, Ammeter, Frequency, Water temperature gauge, Battery condition meter, Hours run meter, Mode selector (Auto, Run, Off), Set mounted MCCB cubicle for the Genset.
SPECIALTIES | Temporary staging area | lot | 15% | 10% | 25% | Excavation works | lot | 15% | 10% | 25% | Concrete on beam | cu.m | 15% | 10% | 25% | Load bearing blocks | sqm | 15% | 10% | 25% | Steel joists (ceiling) | kg | 15% | 10% | 25% | Wooden studs (wall) | bd.ft | 15% | 10% | 25% | Application of joint sealant | lot | 15% | 10% | 25% | Flush hollow core door with viewing window (single) | set/s | 15% | 10% | 25% | Wallpaper finish | sqm | 15% | 10% | 25% | ATM cladding | set/s | 15% | 10% | 25% | L-type modular workstation (R&F) | set/s | 0 | 10% | 10% | Selective replacement of pipes and fittings (verify actual sizes) | lot | 15% | 10% | 25% | Kitchen sink (stainless, above-counter type) | set/s | 15% | 10% | 25% | 6.35mmØ copper refrigerant pipe | lm | 15% | 10% | 25% | 167 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 8.0mm sq. THHN stranded (150m/roll) | roll/s | 15% | 10% | 25% | 25.4mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | Rock removal | lot | 15% | 10% | 25% | Concrete paving | cum | 15% | 10% | 25% | Tank trucks | lot | 15% | 10% | 25% | - |  | Concrete mixture/ratio shall be class A. | [7 empty] | a.) Countertop shall be 25mm thick MDF countertop in light gray high pressure laminate (HPL) finish with color matching PVC edging including 75mm diameter grommet holes. b.) Main countertop dimensions: 1500mm x 600mm c.) Side return dimensions: 900mm x 450mm d.) Partition shall be tile-looked system with interlocking gauge #22 steel panel separated by an impregnated honeycomb paper core. Thickness shall be 50mm and trimming shall be aluminum alloy in powder-coated finish color gray. e) Finish shall be blue fabric. f.) Panel raceway shall be hollow for telephone and electrical lines. Provide convenience outlet hole. g.) PVC keyboard tray shall be included. h.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Sink shall be above counter type and stainless steel finish. b.) Preferably with stainer and deep type. c.) Outlet shall fit with plumbing pipe. d.) Provide sample photo/s and specifications for DBP approval. | [8 empty] | 75kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 167kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity | Locknut and bushing shall be hot-dip galvanized steel material. | 1.) ENGINE a.) Rating: 75KVA b.) Engine speed: ≥1500RPM c.) No. of cylinders (Bore/Stroke): ≥4 (80mm/90mm) d.) Displacement: ≥ 1.2L 2.) FUEL SYSTEM a.) Fuel tank capacity: ≥ 60L (Diesel) b.) Lube oil capacity & Coolant Capacity: ≥ 4L, and ≥ 6L 3.) BATTERY PARAMETERS a.) Battery type: ≥ 12V, 65Ah (Lead Acid Battery with suspended, Electrolyte or equivalent) 4.) ALTERNATOR a.) Output rating: ≥ 75KVA (continuous/prime power) b.) Operating Voltage range: 208 to 240V / 330 to 440V c.) Frequency and Power factor: 60Hz ±5%, 0.8 (lagging) d.) No. of phases: 3-phase, 3-wire + ground f.) Voltage regulation: within ±1.5 g.) Insulation type: class H h.) Energizer type: Brushless, rotating energizer with automatic voltage regulator 5.) CONTROL SYSTEM a.) Automatic controller: Integrating digital, programmable network technology for automation & monitoring. b.) Features: Implements an automatic starting / stopping, data measurements, and alarm protection function of the generator set. c.) Accessories: Voltmeter, Ammeter, Frequency, Water temperature gauge, Battery condition meter, Hours run meter, Mode selector (Auto, Run, Off), Set mounted MCCB cubicle for the Genset.
FURNISHINGS | Temporary fencing | lot | 15% | 10% | 25% | Hauling/transfer of ATM | lot | 15% | 10% | 25% | Concrete on upstand beam | cu.m | 15% | 10% | 25% | Custom wall blocks | sqm | 15% | 10% | 25% | Steel floor decking | sqm | 15% | 10% | 25% | Wooden floor decking/flooring | sqm | 15% | 10% | 25% | Application of glass sealant | lot | 15% | 10% | 25% | Flush hollow core door with viewing window (double) | set/s | 15% | 10% | 25% | Laminated vinyl finish -semi-gloss white (walls) | sqm | 15% | 10% | 25% | Bulletin board | set/s | 15% | 10% | 25% | L-type modular workstation (Cashier/BSO) | set/s | 0 | 10% | 10% | Conversion of sprinkler heads | lot | 15% | 10% | 25% | Kitchen sink (stainless, under-counter type) | set/s | 15% | 10% | 25% | 9.52mmØ copper refrigerant pipe | lm | 15% | 10% | 25% | 200 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 20mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | 25.4mm dia EMT conduit (3m/pc) | pc/s | 15% | 10% | 25% | Dewatering | lot | 15% | 10% | 25% | Concrete bricks pavers | sqm | 15% | 10% | 25% | Utility vehicles | lot | 15% | 10% | 25% | - | a.) The ATM shall be transferred from the old branch site to the new branch site b.) Positioning and mounting/bolting on concrete floor shall be included | Concrete mixture/ratio shall be class A. |  |  |  | Glass sealant shall be silicone-synthetic rubber type and shall match glass and/or aluminum frame color. |  | a.) Materials shall be 1/4" thick MDF panel cladding painted white gloss finish. b.) Refer to section at architectural plans. | a.) Bulletin board dimensions: 24" x width x 36" length". b.) Bulletin board shall be made of cork board on 6mm thick plywood with aluminum casing. c.) Refer to bulletin board details at DBP standard booklet. | a.) Countertop shall be 25mm thick MDF countertop in light gray high pressure laminate (HPL) finish with color matching PVC edging including 75mm diameter grommet holes. b.) Main countertop dimensions: 1500mm x 600mm c.) Side return dimensions: 900mm x 450mm d.) Partition shall be tile-looked system with interlocking gauge #22 steel panel separated by an impregnated honeycomb paper core. Thickness shall be 50mm and trimming shall be aluminum alloy in powder-coated finish color gray. e) Finish shall be blue fabric. f.) Panel raceway shall be hollow for telephone and electrical lines. Provide convenience outlet hole. g.) PVC keyboard tray shall be included. h.) Design shall be same or similar as to the photo at DBP standard booklet. | [10 empty] | 80kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 200kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | Conduits shall be hot-dip galvanized steel material and standard product length shall be 3.05m with coupling on one end | 1.) ENGINE a.) Rating: 80KVA b.) Engine speed: ≥1500RPM c.) No. of cylinders (Bore/Stroke): ≥4 (80mm/90mm) d.) Displacement: ≥ 1.2L 2.) FUEL SYSTEM a.) Fuel tank capacity: ≥ 60L (Diesel) b.) Lube oil capacity & Coolant Capacity: ≥ 4L, and ≥ 6L 3.) BATTERY PARAMETERS a.) Battery type: ≥ 12V, 65Ah (Lead Acid Battery with suspended, Electrolyte or equivalent) 4.) ALTERNATOR a.) Output rating: ≥ 80KVA (continuous/prime power) b.) Operating Voltage range: 208 to 240V / 330 to 440V c.) Frequency and Power factor: 60Hz ±5%, 0.8 (lagging) d.) No. of phases: 3-phase, 3-wire + ground f.) Voltage regulation: within ±1.5 g.) Insulation type: class H h.) Energizer type: Brushless, rotating energizer with automatic voltage regulator 5.) CONTROL SYSTEM a.) Automatic controller: Integrating digital, programmable network technology for automation & monitoring. b.) Features: Implements an automatic starting / stopping, data measurements, and alarm protection function of the generator set. c.) Accessories: Voltmeter, Ammeter, Frequency, Water temperature gauge, Battery condition meter, Hours run meter, Mode selector (Auto, Run, Off), Set mounted MCCB cubicle for the Genset.
FIRE SUPPRESSION SYSTEM | Temporary protective walkways | lot | 15% | 10% | 25% | Hauling/transfer of cash vault | lot | 15% | 10% | 25% | Concrete on lintel beam | cu.m | 15% | 10% | 25% | Adobe/earth blocks | sqm | 15% | 10% | 25% | Stainless steel stair railings | lot | 15% | 10% | 25% | Laminated wood decking/flooring | sqm | 15% | 10% | 25% | Joint sealant replacement | lot | 15% | 10% | 25% | Flush hollow core door with kick plate and viewing window (single) | set/s | 15% | 10% | 25% | Acoustic board ceiling (1200mm x 600mm) including runner system | sqm | 15% | 10% | 25% | Acrylic poster holder | set/s | 15% | 10% | 25% | Single modular workstation (R&F) | set/s | 0 | 10% | 10% | Relocation of sprinkler heads | lot | 15% | 10% | 25% | Floor drain with strainer (stainless steel finish) | set/s | 15% | 10% | 25% | 12.70mmØ copper refrigerant pipe | lm | 15% | 10% | 25% | 250 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 25mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | 25.4mm dia EMT elbow | pc/s | 15% | 10% | 25% | Soil filling/backfilling | cum | 15% | 10% | 25% | Adobe/earth bricks pavers | sqm | 15% | 10% | 25% | Crane | lot | 15% | 10% | 25% | - | The cash safe shall be transferred from the old branch site to the new branch site | Concrete mixture/ratio shall be class A. | [5 empty] | a.) Acoustic board size: 1200mm length x 600mm width x 10mm thickness b.) Acoustic board shall be fine fissured, lay-in type. c.) Runner system shall be galvanized iron coated and baked white finish including hanger rod and fixed bracket/steel angle attachments. d.) Refer to ceiling plan at architectural plans. |  | a.) Countertop shall be 25mm thick MDF countertop in light gray high pressure laminate (HPL) finish with color matching PVC edging including 75mm diameter grommet holes. b.) Countertop dimensions: 1500mm x 600mm c.) Partition shall be tile-looked system with interlocking gauge #22 steel panel separated by an impregnated honeycomb paper core. Thickness shall be 50mm and trimming shall be aluminum alloy in powder-coated finish color gray. d) Finish shall be blue fabric. e.) Panel raceway shall be hollow for telephone and electrical lines. Provide convenience outlet hole. f.) PVC keyboard tray shall be included. g.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Floor drain dimensions: 100mm x 100mm b.) Floor drain shall have multi-layered grating/drainer and shall be in stainless steel finish. c.) Refer to location of floor drain at plumbing plans. | [8 empty] | 100kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 250kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | Elbow shall be hot-dip galvanized steel material.
PLUMBING | Temporary barriers/enclosures | lot | 15% | 10% | 25% | Dismantling works | lot | 15% | 10% | 25% | Concrete on bond beam | cu.m | 15% | 10% | 25% | Terra cotta/clay blocks | sqm | 15% | 10% | 25% | Fabricated steel platform | lot | 15% | 10% | 25% | Engineered wood decking/flooring | sqm | 15% | 10% | 25% | Bituminous dampproofing | sqm | 15% | 10% | 25% | Flush hollow core door with kick plate and viewing window (double) | set/s | 15% | 10% | 25% | Aluminum board ceiling | sqm | 15% | 10% | 25% | Operable wall system | lot | 15% | 10% | 25% | Table with modesty panel (Head) | set/s | 0 | 10% | 10% | Testing and commissioning | lot | 15% | 10% | 25% | Floor drain with rubber plug (stainless steel finish) | set/s | 15% | 10% | 25% | 15.87mmØ copper refrigerant pipe | pc/s | 15% | 10% | 25% | 333 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 32mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | 25.4mm dia EMT coupling and connector (compression type) | set/s | 15% | 10% | 25% | Soil backfilling and compaction | lot | 15% | 10% | 25% | Terra cotta/clay bricks pavers | sqm | 15% | 10% | 25% | Boom lift | lot | 15% | 10% | 25% | a.) Board-up shall be made of galvanized steel fence panel (including opening towards the interior) and placed two (2) feet away from the proposed exterior wall. b.) Floor mat outside hoarding area and plastic sheeting shall be placed on gaps and openings to prevent dust and from entering adjacent unit or common spaces (if applicable). | a.) All dismantled items/materials shall be turned-over to Lessor b.) Refer to as-found/demolition plan | Concrete mixture/ratio shall be class A. |  | a.) Platform height: 100mm b.) Contractor shall verify actual length and width of platform. c.) Platform shall be made of 3/4" thick fiber cement board panel on 2" x 2" x 6mm thick angle bar framing spaced 0.60m both ways and bolted on slab. | [5 empty] | a.) Countertop shall be 25mm thick MDF countertop in light gray high pressure laminate (HPL) finish with color matching PVC edging including 75mm diameter grommet holes. b.) Main countertop dimensions: 1600mm x 700mm c.) Side return dimensions: 900mm x 450mm d.) Stand/support shall be made of tubular steel frame in powder coated finish and gauge #22 perforated modesty panel folded on sides. e.) Design shall be same or similar as to the photo at DBP standard booklet. | [10 empty] | 125kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 333kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | Coupling and connector shall be hot-dip galvanized steel material. | 1.) ENGINE a.) Rating: 125KVA b.) Engine speed: ≥1500RPM c.) No. of cylinders (Bore/Stroke): ≥4 (80mm/90mm) d.) Displacement: ≥ 1.2L 2.) FUEL SYSTEM a.) Fuel tank capacity: ≥ 60L (Diesel) b.) Lube oil capacity & Coolant Capacity: ≥ 4L, and ≥ 6L 3.) BATTERY PARAMETERS a.) Battery type: ≥ 12V, 65Ah (Lead Acid Battery with suspended, Electrolyte or equivalent) 4.) ALTERNATOR a.) Output rating: ≥ 125KVA (continuous/prime power) b.) Operating Voltage range: 208 to 240V / 330 to 440V c.) Frequency and Power factor: 60Hz ±5%, 0.8 (lagging) d.) No. of phases: 3-phase, 3-wire + ground f.) Voltage regulation: within ±1.5 g.) Insulation type: class H h.) Energizer type: Brushless, rotating energizer with automatic voltage regulator 5.) CONTROL SYSTEM a.) Automatic controller: Integrating digital, programmable network technology for automation & monitoring. b.) Features: Implements an automatic starting / stopping, data measurements, and alarm protection function of the generator set. c.) Accessories: Voltmeter, Ammeter, Frequency, Water temperature gauge, Battery condition meter, Hours run meter, Mode selector (Auto, Run, Off), Set mounted MCCB cubicle for the Genset.
HVAC | Temporary project signage/billboard | lot | 9% | 10% | 17% | Hauling of furnitures from the old branch site | lot | 15% | 10% | 25% | Concrete on vault beam | cu.m | 15% | 10% | 25% | Glass block/masonry unit | sqm | 15% | 10% | 25% | Fabricated metal ramp | lot | 15% | 10% | 25% | Wooden baseboards | l.m | 15% | 10% | 25% | Cementitious dampproofing | sqm | 15% | 10% | 25% | Flush hollow core door (low height) - 600mm width | set/s | 15% | 10% | 25% | Plaster and gypsum board (ceiling) | sqm | 15% | 10% | 25% | Parking signage | set/s | 15% | 10% | 25% | Back cabinet (Head) | set/s | 0 | 10% | 10% | Tapping to main line | lot | 15% | 10% | 25% | Wall-mounted faucet (stainless, lever handle) | set/s | 15% | 10% | 25% | 15mmØ PVC drain pipe (3m/pc) with coupling and adapter | pc/s | 15% | 10% | 25% | 500 kVA single phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 40mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | 20mmØ flexible PVC pipe (50m/roll) | roll/s | 15% | 10% | 25% | Soil embankment | cum | 15% | 10% | 25% | Pervious pavers | sqm | 15% | 10% | 25% | Pile driver | lot | 15% | 10% | 25% | Project billboard shall be 4" width x 8' length tarpaulin on 1/2" thick marine plywood provided with necessary frame or support to mount the billboard (refer to IRR of PD 1096 S.2005 Section 306 Figure III.5) | The following furnitures shall be transferred from the old branch site to the new branch site: 1. Guard's podium 2. Poster module 3. Flag stand 4. Forex rate board | Concrete mixture/ratio shall be class A. |  | Refer to fabrication details at DBP standard booklet |  |  | a.) Door dimensions: 600mm width x 900mm length/height x 44.5mm thickness. b.) Materials shall be 6mm thick marine plywood on both sides (flush hollow core) and with kiln-dried tanguile framing. c.) Door jamb shall be 50mm x 100mm using solid kiln dried tanguile wood d.) Refer to schedule of doors at DBP standard booklet. | a.) Materials shall be 12.5mm thick moisture resistant gypsum board screw attached on 2" GI double furring channel spaced 0.60m on center. b.) Hanger rods, clips, carrying channels and all necessary accessories in order to mounth the ceiling shall be included. c.) Hanger rods shall be 6mm dia. bar. d.) All sides attached to wall shall be provided with wall angle. e.) Refer to ceiling plan at architectural plans. |  | a.) Countertop shall be 25mm thick MDF countertop in light gray high pressure laminate (HPL) finish with color matching PVC edging including 75mm diameter grommet holes. b.) Main countertop dimensions: 1600mm x 700mm c.) Side return dimensions: 900mm x 450mm d.) Stand/support shall be made of tubular steel frame in powder coated finish and gauge #22 perforated modesty panel folded on sides. e.) Design shall be same or similar as to the photo at DBP standard booklet. | [10 empty] | 131kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | PVC conduits and fittings shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Capacity: 500kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness, compression and impact resistant, non-corrosive, weatherproof | 1.) ENGINE a.) Rating: 130KVA b.) Engine speed: ≥1500RPM c.) No. of cylinders (Bore/Stroke): ≥4 (80mm/90mm) d.) Displacement: ≥ 1.2L 2.) FUEL SYSTEM a.) Fuel tank capacity: ≥ 60L (Diesel) b.) Lube oil capacity & Coolant Capacity: ≥ 4L, and ≥ 6L 3.) BATTERY PARAMETERS a.) Battery type: ≥ 12V, 65Ah (Lead Acid Battery with suspended, Electrolyte or equivalent) 4.) ALTERNATOR a.) Output rating: ≥ 130KVA (continuous/prime power) b.) Operating Voltage range: 208 to 240V / 330 to 440V c.) Frequency and Power factor: 60Hz ±5%, 0.8 (lagging) d.) No. of phases: 3-phase, 3-wire + ground f.) Voltage regulation: within ±1.5 g.) Insulation type: class H h.) Energizer type: Brushless, rotating energizer with automatic voltage regulator 5.) CONTROL SYSTEM a.) Automatic controller: Integrating digital, programmable network technology for automation & monitoring. b.) Features: Implements an automatic starting / stopping, data measurements, and alarm protection function of the generator set. c.) Accessories: Voltmeter, Ammeter, Frequency, Water temperature gauge, Battery condition meter, Hours run meter, Mode selector (Auto, Run, Off), Set mounted MCCB cubicle for the Genset.
ELECTRICAL | Mobilization and demobilization | lot | 0 | 0 | 0 | Refurbishing of furnitures from the old branch site | lot | 15% | 10% | 25% | Concrete on parapet wall | cu.m | 15% | 10% | 25% | Concrete bricks | sqm | 15% | 10% | 25% | Fabricated metal canopy | lot | 15% | 10% | 25% | Wood cornices | l.m | 15% | 10% | 25% | Sheet dampproofing | sqm | 15% | 10% | 25% | Flush hollow core door (low height) - 700mm width | set/s | 15% | 10% | 25% | Plaster and perforated gypsum board (ceiling) | sqm | 15% | 10% | 25% | Decal - "ATM Hotline 24/7" | set/s | 15% | 10% | 25% | Gang chair (3 seater) | set/s | 0 | 10% | 10% | ABC fire extinguisher (10lbs) | sets | 15% | 10% | 25% | Wall-mounted faucet (stainless, mixer handle) | set/s | 15% | 10% | 25% | 20mmØ PVC drain pipe (3m/pc) with coupling and adapter | pc/s | 15% | 10% | 25% | 5 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 110mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | 20mmØ straight connector | pc/s | 15% | 10% | 25% | Rodent control | lot | 15% | 10% | 25% | Cobblestone | sqm | 15% | 10% | 25% | Wheel loaders | lot | 15% | 10% | 25% | - | The following furnitures shall be refurbished and shall look brand new upon delivery on site: 1. Guard's podium 2. Poster module 3. Flag stand | Concrete mixture/ratio shall be class A. |  | Refer to fabrication details at DBP standard booklet |  |  | a.) Door dimensions: 700mm width x 900mm length/height x 44.5mm thickness. b.) Materials shall be 6mm thick marine plywood on both sides (flush hollow core) and with kiln-dried tanguile framing. c.) Door jamb shall be 50mm x 100mm using solid kiln dried tanguile wood d.) Refer to schedule of doors at DBP standard booklet. |  |  | a.) Chair shall be 3 seater, made of black leatherette moulded foam cushion upholstered backrest and seat; 1.4 mm thickness perforated metal seats sprayed with static powder after anti rust treatment; with armrest, steel frame legs and matte silver steel base. b.) Seat dimensions shall be minimum of 500mm x 470mm. c.) Backrest dimensions shall be minimum of 2500mm length x 630mm width/depth x 800mm height d.) Design shall be same or similar as to the photo at DBP standard booklet. | a.) Capacity shall be 10lbs. b.) Chemical shall be hexfluoropropane. c.) Fire extinguisher shall be wall mounted. d.) Fire extinguisher shall be BFP approved. e.) Refer to fire protection plans for fire extinguisher location. | [9 empty] | 150kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | PVC conduits and fittings shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Capacity: 5kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | Straight connector shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | 1.) ENGINE a.) Rating: 150KVA b.) Engine speed: ≥1500RPM c.) No. of cylinders (Bore/Stroke): ≥4 (80mm/90mm) d.) Displacement: ≥ 1.2L 2.) FUEL SYSTEM a.) Fuel tank capacity: ≥ 60L (Diesel) b.) Lube oil capacity & Coolant Capacity: ≥ 4L, and ≥ 6L 3.) BATTERY PARAMETERS a.) Battery type: ≥ 12V, 65Ah (Lead Acid Battery with suspended, Electrolyte or equivalent) 4.) ALTERNATOR a.) Output rating: ≥ 150KVA (continuous/prime power) b.) Operating Voltage range: 208 to 240V / 330 to 440V c.) Frequency and Power factor: 60Hz ±5%, 0.8 (lagging) d.) No. of phases: 3-phase, 3-wire + ground f.) Voltage regulation: within ±1.5 g.) Insulation type: class H h.) Energizer type: Brushless, rotating energizer with automatic voltage regulator 5.) CONTROL SYSTEM a.) Automatic controller: Integrating digital, programmable network technology for automation & monitoring. b.) Features: Implements an automatic starting / stopping, data measurements, and alarm protection function of the generator set. c.) Accessories: Voltmeter, Ammeter, Frequency, Water temperature gauge, Battery condition meter, Hours run meter, Mode selector (Auto, Run, Off), Set mounted MCCB cubicle for the Genset.
POWER GENERATING EQUIPMENT | Lay-out/staking | lot | 15% | 10% | 25% | [5 empty] | Concrete on zocalo | cu.m | 15% | 10% | 25% | Adobe/earth bricks | sqm | 15% | 10% | 25% | Fabricated TV bracket anchor | set/s | 15% | 10% | 25% | Wood fascia | sqm | 15% | 10% | 25% | Bituminous torch membrane waterproofing | sqm | 15% | 10% | 25% | Flush hollow core door (low height) - 800mm width | set/s | 15% | 10% | 25% | Spandrel ceiling | sqm | 15% | 10% | 25% | Decal - "Reserved for DBP Clients" | set/s | 15% | 10% | 25% | Gang chair (4 seater) | set/s | 0 | 10% | 10% | [5 empty] | Wall-mounted faucet (stainless, double-lever handle) | set/s | 15% | 10% | 25% | 3/4" dia PVC drain pipe (3m/pc) with coupling and adapter | pc/s | 15% | 10% | 25% | 10 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 20mm dia PVC elbow | pc/s | 15% | 10% | 25% | 20mmØ angle connector | pc/s | 15% | 10% | 25% | Termite control | lot | 15% | 10% | 25% | Concrete curbs and gutters | cum | 15% | 10% | 25% | Skid steer | lot | 15% | 10% | 25% | Initial site layout shall be approved by DBP before proceeding with any civil works (if applicable). |  | Concrete mixture/ratio shall be class B. |  | Refer to fabrication details at DBP standard booklet |  | Waterproofing shall be mineral polybond 4.5kg torch-on membrane waterproofing. | a.) Door dimensions: 800mm width x 900mm length/height x 44.5mm thickness. b.) Materials shall be 6mm thick marine plywood on both sides (flush hollow core) and with kiln-dried tanguile framing. c.) Door jamb shall be 50mm x 100mm using solid kiln dried tanguile wood d.) Refer to schedule of doors at DBP standard booklet. |  |  | a.) Chair shall be 4 seater, made of black leatherette moulded foam cushion upholstered backrest and seat; 1.4 mm thickness perforated metal seats sprayed with static powder after anti rust treatment; with armrest, steel frame legs and matte silver steel base. b.) Seat dimensions shall be minimum of 500mm x 470mm. c.) Backrest dimensions shall be minimum of 2500mm length x 630mm width/depth x 800mm height d.) Design shall be same or similar as to the photo at DBP standard booklet. | [10 empty] | 169kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | PVC conduits and fittings shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Capacity: 10kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Elbow shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | Angle connector shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
COMMUNICATIONS | Site cleaning | lot | 15% | 10% | 25% | [5 empty] | Concrete on canopy | cu.m | 15% | 10% | 25% | Terra cotta/clay bricks | sqm | 15% | 10% | 25% | Fabricated wall-type flagpole | lot | 15% | 10% | 25% | Wooden partition | sqm | 15% | 10% | 25% | Elastomeric paint waterproofing | sqm | 15% | 10% | 25% | Flush hollow core door (low height) - 900mm width | set/s | 15% | 10% | 25% | PVC ceiling | sqm | 15% | 10% | 25% | Poster - "No Noon Break" | set/s | 15% | 10% | 25% | High back chair (Head) | set/s | 0 | 10% | 10% | [5 empty] | Wall-mounted faucet (stainless, double-mixer handle) | set/s | 15% | 10% | 25% | Rubber insulation (1/2" thk) | lm | 15% | 10% | 25% | 15 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 25mm dia PVC elbow | pc/s | 15% | 10% | 25% | Hanger and support | lot | 15% | 10% | 25% | Soil poisoning | lot | 15% | 10% | 25% | Concrete steps and ramps | cu.m | 15% | 10% | 25% | Flat bed trucks | lot | 15% | 10% | 25% | a.) Daily site cleaning shall be required. b.) Final and thorough cleaning shall be done prior to turn-over of site to DBP. |  | Concrete mixture/ratio shall be class A. |  | Refer to fabrication details at DBP standard booklet |  |  | a.) Door dimensions: 900mm width x 900mm length/height x 44.5mm thickness. b.) Materials shall be 6mm thick marine plywood on both sides (flush hollow core) and with kiln-dried tanguile framing. c.) Door jamb shall be 50mm x 100mm using solid kiln dried tanguile wood d.) Refer to schedule of doors at DBP standard booklet. |  |  | a.) Chair shall be made of high back black leatherette cushion seat with molded foam- cushion upholstered backrest; padded armrest; gas lift; chrome plated star base; tilting/swivel mechanism and twin caster. b.) Seat dimensions shall be minimum of 550mm x 600mm. c.) Backrest dimensions shall be minimum of 520mm x 740mm e.) Chair height shall be minimum of 1200mm (adjustable height) f.) Design shall be same or similar as to the photo at DBP standard booklet. | [10 empty] | 175kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 15kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Elbow shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | Hanger rod shall be 6mm dia. bar with expansion shield and bolted on underslab.
ELECTRONIC SAFETY AND SECURITY | Hauling/disposal | lot | 15% | 10% | 25% | [5 empty] | Concrete on platform | cu.m | 15% | 10% | 25% | Selective demolition of masonry wall | lot | 15% | 10% | 25% | Fabricated signage pole/stand | lot | 15% | 10% | 25% | Plywood ceiling | sqm | 15% | 10% | 25% | Polyurethane liquid membrane waterproofing | sqm | 15% | 10% | 25% | Flush hollow core door (concealed) - 700mm width | set/s | 15% | 10% | 25% | Polished homogenous tile finish - white (flooring) | sqm | 15% | 10% | 25% | Poster - "Contact Center ng Bayan" | set/s | 15% | 10% | 25% | Mid back chair with arm rest (Junior Officer) | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, lever handle, standard spout) | set/s | 15% | 10% | 25% | Rubber insulation (3/4" thk) | lm | 15% | 10% | 25% | 25 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 32mm dia PVC elbow | pc/s | 15% | 10% | 25% | Consumables (tape, tagging, PVC cement and accessories) | lot | 0% | 10% | 10% | Gravel bedding | cum | 15% | 10% | 25% | Concrete sidewalk | cum | 15% | 10% | 25% | Heavy hauler | lot | 15% | 10% | 25% | a.) All old materials, trash, debris, including hazardous waste (spills) shall be removed from the immediate work area as the work progresses. It shall be carefully piled up and/or properly seggregated in a appropriate container before disposal. b.) Weekly hauling is required. |  | Concrete mixture/ratio shall be class A. |  | Refer to fabrication details at DBP standard booklet |  |  | a.) Door dimensions: 700mm width x 2100mm length/height x 44.5mm thickness. b.) Materials shall be 6mm thick marine plywood on both sides (flush hollow core) and with kiln-dried tanguile framing. c.) Door jamb shall be 50mm x 100mm using solid kiln dried tanguile wood d.) Refer to schedule of doors at DBP standard booklet. | a.) Tile size: 600mm x 600mm (verify applicable thickness) b.) Tiles shall be polished homogenous tiles (full body porcelain tiles) with white finish. c.) Contractor shall provide sample/s for DBP approval. d.) Refer to tiling layout at architectural plans. |  | a.) Chair shall be made of fabric molded foam-cushion upholstered seat and backrest; gas lift; with armrest; nylon star base with twin caster; tilting/swivel mechanism. b.) Fabric color shall be twilight blue. c.) Seat dimensions shall be minimum of 500mm x 470mm. d.) Backrest dimensions shall be minimum of 550mm x 500mm e.) Chair height shall be minimum of 910mm (adjustable height) f.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Faucet shall be above-counter mounted, stainless steel finish with lever handle and standard spout. b.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 188kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 25kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Elbow shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | All necessary consumables to complete the electrical works shall be included.
EARTHWORK | As-built plans | lot | 15% | 10% | 25% | [5 empty] | Concrete on counter (lavatory) | cu.m | 15% | 10% | 25% | Selective restoration of masonry wall | lot | 15% | 10% | 25% | Fabricated louvers | lot | 15% | 10% | 25% | Plywood partition | sqm | 15% | 10% | 25% | Pedestrian traffic coatings | lot | 15% | 10% | 25% | Flush hollow core door (concealed) - 800mm width | set/s | 15% | 10% | 25% | Polished homogenous tile finish - gray (flooring) | sqm | 15% | 10% | 25% | Poster - "No to Fixers" | set/s | 15% | 10% | 25% | Mid back chair without arm rest (Conference Room) | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, mixer handle, standard spout) | set/s | 15% | 10% | 25% | Rubber insulation (7/8" thk) | lm | 15% | 10% | 25% | 37.5 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 63mm dia PVC elbow | pc/s | 15% | 10% | 25% | Junction box with cover (ga#16) | set/s | 15% | 10% | 25% | Vegetation control | lot | 15% | 10% | 25% | Concrete driveways | cum | 15% | 10% | 25% | Graders | lot | 15% | 10% | 25% | Three (3) sets of blueprint signed and sealed; and CAD file shall be be sent thru email |  | Concrete mixture/ratio shall be class B. |  | Refer to fabrication details at DBP standard booklet |  |  | a.) Door dimensions: 800mm width x 2100mm length/height x 44.5mm thickness. b.) Materials shall be 6mm thick marine plywood on both sides (flush hollow core) and with kiln-dried tanguile framing. c.) Door jamb shall be 50mm x 100mm using solid kiln dried tanguile wood d.) Refer to schedule of doors at DBP standard booklet. | a.) Tile size: 600mm x 600mm (verify applicable thickness) b.) Tiles shall be polished homogenous tiles (full body porcelain tiles) with gray finish. c.) 3mm tile grout matching the tile color shall be provided. d) Contractor shall provide samples for DBP approval. e.) Refer to tiling layout at architectural plans. |  | a.) Chair shall be made of fabric molded foam-cushion upholstered seat and backrest; without armrest; gas lift; nylon star base with twin caster; tilting/swivel mechanism. b.) Fabric color shall be twilight blue. c.) Seat dimensions shall be minimum of 500mm x 470mm. d.) Backrest dimensions shall be minimum of 550mm x 500mm e.) Chair height shall be minimum of 910mm (adjustable height) f.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Faucet shall be above-counter mounted, stainless steel finish with mixer handle and standard spout. b.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 200kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 37.5kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Elbow shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Junction box dimensions: 4" x 4" (GA#16) b.) Junction box deep type with cover and shall be made of galvanized iron.
EXTERIOR IMPROVEMENTS | [10 empty] | Concrete on counter (kitchen sink) | cu.m | 15% | 10% | 25% | CHB wall - 6" (retaining wall) | sqm | 15% | 10% | 25% | Fabricated vault grilles | lot | 15% | 10% | 25% | Wood stairs | lot | 15% | 10% | 25% | Vehicular traffic coatings | lot | 15% | 10% | 25% | Flush hollow core door (laminated) | set/s | 15% | 10% | 25% | Non-skid homogenous tile finish - light brown (flooring) | sqm | 15% | 10% | 25% | Poster - "No Gift Policy" | set/s | 15% | 10% | 25% | Teller's chair | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, pull-out handle, standard spout) | set/s | 15% | 10% | 25% | Fittings | lot | 15% | 10% | 25% | 50 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 110mm dia PVC elbow | pc/s | 15% | 10% | 25% | Utility box (ga#16) | set/s | 15% | 10% | 25% | Geosynthetics | sqm | 15% | 10% | 25% | Concrete parking bumpers | set/s | 15% | 10% | 25% | Concrete boom | lot | 15% | 10% | 25% |  |  | Concrete mixture/ratio shall be class B. | a.) CHB shall be 700 PSI compressive strength (minimum) provided with test results, normal in weight and in conformance to ASTM C-90, Type 1. b.) Rebar diameter shall be 10mm. c.) Concrete filler mixture/ratio shall be class A. d.) Both sides shall be plastered e.) Refer to CHB wall details at DBP standard booklet. | Refer to fabrication details at DBP standard booklet |  |  |  | a.) Tile size: 600mm x 600mm (verify applicable thickness) b.) Tiles shall be non-skid/slip homogenous tiles (full body porcelain tiles) with brown finish. c.) 3mm tile grout matching the tile color shall be provided. d.) Contractor shall provide samples for DBP approval. e.) Refer to tiling layout at architectural plans. |  | a.) Chair materials shall be fabric moulded-cushion upholstered backrest and seat, without armrest; gas lift; tilting/swivel mechanism; five (5) legged with foot ring and fixed base. b.) Fabric color shall be twilight blue. c.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Faucet shall be above-counter mounted, stainless steel finish with pull-out handle and standard spout. b.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 225kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 50kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Elbow shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Utility box dimensions: 4" x 2" (GA#16) b.) Utility box deep type and shall be made of galvanized iron.
HANDLING EQUIPMENT | [10 empty] | Concrete on stairs | cu.m | 15% | 10% | 25% | CHB wall - 4" (parapet wall) | sqm | 15% | 10% | 25% | Fabricated AC indoor unit platform | set/s | 15% | 10% | 25% | Wood railings | lot | 15% | 10% | 25% | 1" thk. polyethylene (PE) foam insulation (double sided) | sqm | 15% | 10% | 25% | Flush hollow core door (double) | set/s | 15% | 10% | 25% | Rustic tiles with pebble washout nosing | sqm | 15% | 10% | 25% | Poster - "Citizen's Charter" | set/s | 15% | 10% | 25% | Staff chair (R&F) | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, touchless, standard spout) | set/s | 15% | 10% | 25% | Consumables (torch, refrigerant, tape, taging, PVC cement and accessories) | lot | 0% | 10% | 10% | 75 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 20mm dia PVC coupling | pc/s | 15% | 10% | 25% | Pullbox (ga#16) | set/s | 15% | 10% | 25% | Geotextiles | sqm | 15% | 10% | 25% | Concrete plantbox/es | lot | 15% | 10% | 25% | [7 empty] | Concrete mixture/ratio shall be class A. |  | a.) Material shall 1 1/2" x 1 1/2" thick angle bar and fully-welded on joints. b) Refer to miscellaneous details at mechanical plan. |  |  |  | a.) Tile size: 600mm x 600mm (verify applicable thickness) b.) Tiles shall be non-skid/slip rustic tiles (full body porcelain tiles) for exterior use. c.) 3mm tile grout matching the tile color shall be provided. d.) Contractor shall provide sample/s for DBP approval. e.) Refer to tiling layout at architectural plans. |  | a.) Chair shall be made of fabric molded foam-cushion upholstered seat and backrest; gas lift; with arm rest; nylon star base with twin caster; tilting/swivel mechanism. b.) Fabric color shall be twilight blue. c.) Seat dimensions shall be minimum of 500mm x 470mm. d.) Backrest dimensions shall be minimum of 450mm x 500mm e.) Chair height shall be minimum of 880mm (adjustable height) f.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Faucet shall be above-counter mounted, stainless steel finish with automatic sensor and standard spout. b.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 250kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | All necessary consumables to complete the HVACl works shall be included. | a.) Capacity: 75kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Coupling shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Pullbox dimensions: 24"x 24" x 16" (GA#16) b.) Pullbox material shall be made of galvanized iron. | 1.) ENGINE a.) Rating: 250KVA b.) Engine speed: ≥1500RPM c.) No. of cylinders (Bore/Stroke): ≥4 (80mm/90mm) d.) Displacement: ≥ 1.2L 2.) FUEL SYSTEM a.) Fuel tank capacity: ≥ 60L (Diesel) b.) Lube oil capacity & Coolant Capacity: ≥ 4L, and ≥ 6L 3.) BATTERY PARAMETERS a.) Battery type: ≥ 12V, 65Ah (Lead Acid Battery with suspended, Electrolyte or equivalent) 4.) ALTERNATOR a.) Output rating: ≥ 250KVA (continuous/prime power) b.) Operating Voltage range: 208 to 240V / 330 to 440V c.) Frequency and Power factor: 60Hz ±5%, 0.8 (lagging) d.) No. of phases: 3-phase, 3-wire + ground f.) Voltage regulation: within ±1.5 g.) Insulation type: class H h.) Energizer type: Brushless, rotating energizer with automatic voltage regulator 5.) CONTROL SYSTEM a.) Automatic controller: Integrating digital, programmable network technology for automation & monitoring. b.) Features: Implements an automatic starting / stopping, data measurements, and alarm protection function of the generator set. c.) Accessories: Voltmeter, Ammeter, Frequency, Water temperature gauge, Battery condition meter, Hours run meter, Mode selector (Auto, Run, Off), Set mounted MCCB cubicle for the Genset.
[11 empty] | Concrete topping | cu.m | 15% | 10% | 25% | CHB wall - 4" (zocalo) | sqm | 15% | 10% | 25% | Fabricated AC outdoor unit platform | set/s | 15% | 10% | 25% | Fiber glass panels | set/s | 15% | 10% | 25% | Cellulose fiber glass wool insulation | sqm | 15% | 10% | 25% | Wooden louver door (single) | set/s | 15% | 10% | 25% | Vinyl tiles flooring - cottage tan | sqm | 15% | 10% | 25% | Poster - "DBP Corporate Philosophy" | set/s | 15% | 10% | 25% | Visitor's chair | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, double-lever handle, standard spout) | set/s | 15% | 10% | 25% | Hangers and support | lot | 15% | 10% | 25% | 100 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 25mm dia PVC coupling | pc/s | 15% | 10% | 25% | Fire alarm control panel (FACP) | set/s | 15% | 10% | 25% | Geomembranes | sqm | 15% | 10% | 25% | Metal bollards | set/s | 15% | 10% | 25% | [7 empty] | Concrete mixture/ratio shall be class B. |  | a.) Material shall 1 1/2" x 1 1/2" thick angle bar and fully-welded on joints. b) Refer to miscellaneous details at mechanical plan. |  |  |  | a.) Tile size: 300mm x 300mm (verify applicable thickness) b.) Tiles shall be vinyl finish (cottage tan). c.) Self-leveling grout shall be applied prior to tiles installation. d.) Contractor shall provide sample/s for DBP approval. e.) Refer to tiling layout at architectural plans. |  | a.) Chair shall be made of fabric molded foam-cushion upholstered seat and backrest; without arm rest; powder coated steel frame gauge 20 (sled type leg) b.) Fabric color shall be twilight blue. c.) Seat dimensions shall be minimum of 450mm x 450mm. d.) Backrest dimensions shall be minimum of 460mm x 320mm e.) Chair height shall be minimum of 800mm f.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Faucet shall be above-counter mounted, stainless steel finish with double-lever handle and standard spout. b.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 300kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | Hanger rod shall be 6mm dia. bar with expansion shield and bolted on underslab. | a.) Capacity: 100kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Coupling shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[11 empty] | Concrete coring including pipe sleeve/s | lot | 15% | 10% | 25% | [5 empty] | Fabricated AC outdoor unit cage | set/s | 15% | 10% | 25% | Polycarbonate sheets/panels | set/s | 15% | 10% | 25% | Polyurethane foam coating insulation | sqm | 15% | 10% | 25% | Wooden louver door (double) | set/s | 15% | 10% | 25% | Anti-static vinyl flooring | sqm | 15% | 10% | 25% | Poster - "Environmental Policy Statement" | set/s | 15% | 10% | 25% | Pantry chair | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, double-mixer handle, standard spout) | set/s | 15% | 10% | 25% | Testing and commissioning | lot | 15% | 10% | 25% | 150 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 32mm dia PVC coupling | pc/s | 15% | 10% | 25% | Heat detector (addressable) | set/s | 15% | 10% | 25% | Geogrids | sqm | 15% | 10% | 25% | Steel gate (vehicular) | lot | 15% | 10% | 25% | [7 empty] | a.) Rebar scanning must be conducted prior to concrete coring. b.) Actual diameter and number of hole/s shall be verified on site. |  | a.) Cage shall be made of 50mm x 50mm tubular channel grills, tubular framing including fabricated hinges and barrel bolt. b.) Refer to fabrication details at schedule of grills details. | [5 empty] | a.) Stool chair with leatherette foam cushion seat; without armrest and backrest; 1” x 1” powder coated tubular steel frame gauge 20. b.) Seat finish shall be black leatherette. c.) Seat dimensions shall be minimum of 330mm x 330mm. d.) Chair height shall be minimum of 460mm e.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Faucet shall be above-counter mounted, stainless steel finish with double-mixer handle and standard spout. b.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 330kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | Contractor shall holds responsibilities for mounting termination, testing and commissioning and programming to ensure that every component and system is operational | a.) Contractor shall provide and install pad/pole-mounted 150kVA, 3Φ distribution transformer with rated 60Hz b.) The contractor shall ensure the cooling class type; Oil immersed, self-cooled (non-PCB type) c.) Contractor to use mineral oil for insulation fluid and copper for winding with temperature rise of winding not to exceed 65ºC d.) Contractor to install all necessary standard mounting accessories. e.) Contractor shall submit all documents and pay all the fees necessary for permanent power application | Coupling shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[11 empty] | Concrete epoxy injection | lot | 15% | 10% | 25% | [5 empty] | Fabricated water meter cage | set/s | 15% | 10% | 25% | Pantry cabinet (undercounter) | set/s | 15% | 10% | 25% | Asphalt shingles roofing | sqm | 15% | 10% | 25% | Sliding wood door (single) | set/s | 15% | 10% | 25% | Raised flooring | sqm | 15% | 10% | 25% | Poster - "Quality Policy" | set/s | 15% | 10% | 25% | Steel shelves | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, pull-down handle, gooseneck spout) | set/s | 15% | 10% | 25% | Existing AC system cleaning and maintenance | lot | 15% | 10% | 25% | 167 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 63mm dia PVC coupling | pc/s | 15% | 10% | 25% | Smoke detector (addressable) | set/s | 15% | 10% | 25% | Sheet piling | lot | 15% | 10% | 25% | Steel gate (pedestrian) | lot | 15% | 10% | 25% | [9 empty] | - | [5 empty] | a.) Minimum shelves dimensions: 400mm width x 1840mm height x 900mm length x 5 layers b.) Shelves shall be boltless, adjustable and in all steel materials. c.) Design shall be same or similar as to the photo at DBP standard booklet. |  | a.) Faucet shall be above-counter mounted, stainless steel finish with pull-down handle and gooseneck spout. b.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 440kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 167kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Coupling shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[11 empty] | Selective demolition of concrete | lot | 15% | 10% | 25% | [5 empty] | Fabricated electric meter cage | set/s | 15% | 10% | 25% | Pantry cabinet (overhead) | set/s | 15% | 10% | 25% | Corrugated GI sheet roofing | sqm | 15% | 10% | 25% | Sliding wood door (double) | set/s | 15% | 10% | 25% | Engineered wood flooring | sqm | 15% | 10% | 25% | Poster - "Family Credo" | set/s | 15% | 10% | 25% | Steel locker (6 holes) | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, lever handle, gooseneck spout) | set/s | 15% | 10% | 25% | Existing AC system relocation | lot | 15% | 10% | 25% | 200 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 110mm dia PVC coupling | pc/s | 15% | 10% | 25% | Digital optical detector with base | pc/s | 15% | 10% | 25% | Metal hydraulic shoring | lot | 15% | 10% | 25% | Steel fence | lot | 15% | 10% | 25% | [9 empty] | - | Refer to fabrication details at DBP standard booklet. |  |  |  |  | a.) Locker dimensions: 72" height x 36" width x 18" depth b.) Openings/holes: six (6) c.) Opening dimensions: 31" height x 10" width d.) Locker color shall be beige. Materials as per manufacturer's standard. e.) Louvers, aluminum card holder, lock hasp, chrome plated handle, hanger rod on top and bottom shelf shalle be included. f.) Refer to locker details at DBP standard booklet. |  | a.) Faucet shall be above-counter mounted, stainless steel finish with lever handle and gooseneck spout. b.) Design shall be same or similar as to the photo at DBP standard booklet. | [8 empty] | 500kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 200kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Coupling shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[11 empty] | Selective restoration of concrete | lot | 15% | 10% | 25% | [5 empty] | Fabricated genset housing | lot | 15% | 10% | 25% | Pantry ledge | set/s | 15% | 10% | 25% | Clay tile roofing | sqm | 15% | 10% | 25% | Hollow metal door (single) | set/s | 15% | 10% | 25% | Carpet tiles flooring | sqm | 15% | 10% | 25% | Poster - "Acquired Assets" | set/s | 15% | 10% | 25% | Steel locker (9 holes) | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, mixer handle, gooseneck spout) | set/s | 15% | 10% | 25% | Existing AC ducting relocation and rebranching | lot | 15% | 10% | 25% | 250 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 20mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | Digital dual heat detector with base | pc/s | 15% | 10% | 25% | Underpinning piers | lot | 15% | 10% | 25% | Wire fence with steel post | lot | 15% | 10% | 25% | [9 empty] | a.) Housing shall be made of 50mm x 50mm tubular channel grills, tubular framing including fabricated hinges and barrel bolt. b.) Contractor shall verify genset location and actual measurements of provision on site. | a.) Material shall be 20mm thick marine plywood for partition, shelves and swing-out cabinet doors. b.) Accessories such as concealed pneumatic cabinet hinges and stainless cabinet handles shall be included. c.) All necessary mounting support, frame or backing shall be included. d.) Refer to fabrication details at DBP standard booklet. |  |  |  |  | a.) Locker dimensions: 72" height x 36" width x 18" depth b.) Openings/holes: nine (9) c.) Opening dimensions: 20" height x 10" width d.) Locker color shall be beige. Materials as per manufacturer's standard. e.) Louvers, aluminum card holder, lock hasp, chrome plated handle, hanger rod on top and bottom shelf shalle be included. f.) Refer to locker details at DBP standard booklet. | [10 empty] | 625kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 250kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Adapter and locknut shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[11 empty] | Genset bundwall | lot | 15% | 10% | 25% | [5 empty] | Fabricated metal spiral stairs | lot | 15% | 10% | 25% | Wooden cabinet | set/s | 15% | 10% | 25% | Pre-painted long span aluminum roofing (corrugated) | sqm | 15% | 10% | 25% | Hollow metal door (double) | set/s | 15% | 10% | 25% | Exterior painting (walls) | sqm | 15% | 10% | 25% | Sintra Board - "Temporary Unavailable" | set/s | 15% | 10% | 25% | Steel locker (12 holes) | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, double-lever handle, gooseneck spout) | set/s | 15% | 10% | 25% | Existing AC system removal/dismantling | lot | 15% | 10% | 25% | 333 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 25mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | Manual call point with strobe sounder | set/s | 15% | 10% | 25% | Micropile underpinning | lot | 15% | 10% | 25% | CHB fence | lot | 15% | 10% | 25% | [7 empty] | a.) Bundwall shall be made of recinforced concrete. b.) Verify size of genset prior to construction of bundwall. c.) Refer to budnwall details at DBP standard booklet. | [5 empty] | a.) All masonry/concrete walls shall be applied with masonry neuralizer with 1:16 neuralizer-water ratio. b.) Contractor shall apply masonry putty and ensure that the wall surface is smooth and free from defects prior to painting. c.) Primer acrylic latex paint (color: white) shall be applied to ensure that paint will bond to the wall surface. d.) Two (2) coats of semi-gloss acrylic latex paint (color: white) shall be used for finishing/final coating. | a.) Signage shall be made of 1/4" thick sintra board with print on one side b.) Refer to signage details for design and location. | a.) Locker dimensions: 72" height x 36" width x 18" depth b.) Openings/holes: twelve (12) c.) Opening dimensions: 15" height x 10" width d.) Locker color shall be beige. Materials as per manufacturer's standard. e.) Louvers, aluminum card holder, lock hasp, chrome plated handle, hanger rod on top and bottom shelf shalle be included. f.) Refer to locker details at DBP standard booklet. | [10 empty] | 750kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Capacity: 333kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Adapter and locknut shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[11 empty] | Vault seismic gap | sqm | 15% | 10% | 25% | [5 empty] | Fabricated pull-out ladder | set/s | 15% | 10% | 25% | Vault wooden cabinet (overhead) | set/s | 15% | 10% | 25% | Pre-painted long span aluminum roofing (rib type) | sqm | 15% | 10% | 25% | Fire exit door | set/s | 15% | 10% | 25% | Exterior painting (eaves) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Smoking Area" | set/s | 15% | 10% | 25% | Roll-up blinds | sqft | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, double-mixer handle, gooseneck spout) | set/s | 15% | 10% | 25% | Exhaust fan (ceiling mounted) | set/s | 15% | 10% | 25% | 500 kVA three phase distribution transformer 13.2 kV/7.62 kV primary, 120 V/240 V secondary | lot | 15% | 10% | 25% | 32mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | Digital manual call point | pc/s | 15% | 10% | 25% | Sheet piling cofferdams | lot | 15% | 10% | 25% | Composite fence | lot | 15% | 10% | 25% | [7 empty] | 25mm thick styropore seismic gap |  |  | a.) Material shall be 20mm thick marine plywood with solid edging for partition, shelves and swing-out cabinet doors. b.) Accessories such as concealed pneumatic cabinet hinges and stainless cabinet handles shall be included. c.) All necessary mounting support, frame or backing shall be included. d.) Refer to fabrication details at DBP standard booklet. |  | a.) Door dimensions: 900mm width x 2100mm length/height x 44.5mm thickness. b.) Materials shall be fire rated standard steel plate flush hollow core metal. c.) Door jamb shall be GA 16 rectangular hollow section. d.) Fabricated hinges, panic lever device and peep hole shall be included. e.) Stainless steel cladding on the exterior side shall be included if the door will be exposed to rain. f.) Refer to schedule of doors at DBP standard booklet. |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | a.) Blinds shall be combination of polyester and PVC materials, 0.68-0.70mm thick, has an openness factor of 4-5% and color shall be 'white bone' or equivalent. b.) Accessories such as roller tubes, brackets, control and end caps, plunger system, bottom bars and bead chains shall be included. c.) Roller tube shall be made of aluminum with fabric location slots/strengthening fins. d.) Brackets shall be powder coated white, made of steel and has universal fixing points. e.) Control end and plunger end system shall be spring loaded and white in color. f) Bead chain shall be stainless steel and has a maximum operating weight of 16 lbs. g.) Bottom bar shall be in aluminum white finish and oval in shape to conceal and secure the fabric. h.) End cap shall be provided to prevent the blinds from coming out of the bracket, color/finish is white. i.) Verify actual measurements of windows prior to fabrication of blinds. | [10 empty] | 875kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor to install necessary accessories: hanger & support, mouting accessories, switches | a.) Capacity: 500kVA b.) Primary Voltage: 7.62/13.2kV c.) Secondary Voltage: 120/240V with 2-2.5% Standard Taps FCAC/FCBN d.) Rated Frequency: 60Hz e.) Mounting: Pole-mounted f.) Temperature rise of winding: Not to exceed 65 degrees Celsius g.) Cooling class type: Oil immersed, self-cooled (non-PCB type) h.) Insulation Fluid: Mineral oil i.) Material of winding: All copper j.) Casing/Tank: Based on manufacturer’s product | Adapter and locknut shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[11 empty] | Concrete on footing tie beam | cu.m | 15% | 10% | 25% | [5 empty] | Ladder rung | lot | 15% | 10% | 25% | Back office wooden cabinet (overhead) | set/s | 15% | 10% | 25% | Roofing accessories | lot | 15% | 10% | 25% | Sliding metal door (single) | set/s | 15% | 10% | 25% | Exterior painting (canopy) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Authorized Personnel Only" | set/s | 15% | 10% | 25% | Automatic alcohol dispenser | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, pull-down handle, hose spout) | set/s | 15% | 10% | 25% | Exhaust fan (wall mounted) | set/s | 15% | 10% | 25% | 60kVA, three phase, 400V/230V, 60Hz Step-down Transformer | lot | 15% | 10% | 25% | 40mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | Alarm bell | set/s | 15% | 10% | 25% | Concrete piles (driven piles) | lot | 15% | 10% | 25% | Concrete retaining wall | sqm | 15% | 10% | 25% | [7 empty] | Concrete mixture/ratio shall be class A. |  | - | a.) Material shall be 20mm thick marine plywood with solid edging for partition, shelves, cove and swing-out cabinet doors. b.) Accessories such as concealed pneumatic cabinet hinges and stainless cabinet handles shall be included. c.) All necessary mounting support, frame or backing shall be included. d.) Refer to fabrication details at DBP standard booklet. |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [11 empty] | 1000kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor to install necessary accessories: hanger & support, mouting accessories, switches |  | Adapter and locknut shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[11 empty] | Concrete on parapet wall column | cu.m | 15% | 10% | 25% | [5 empty] | Metal catwalk | lot | 15% | 10% | 25% | Wood drawer | set/s | 15% | 10% | 25% | Selective removal/demolition of roofing | lot | 15% | 10% | 25% | Sliding metal door (double) | set/s | 15% | 10% | 25% | Exterior painting (parapet wall) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Fire Extinguisher" | set/s | 15% | 10% | 25% | Automatic infrared temperature scanner | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, lever handle, hose spout) | set/s | 15% | 10% | 25% | 150mmØ PVC exhaust pipe (3m/pc) | pc/s | 15% | 10% | 25% | Concrete/Steel Pole orTransformer pad with accessories inclusive of pole erection and installation of components | lot | 15% | 10% | 25% | 110mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | Addressable sounder strobe | pc/s | 15% | 10% | 25% | Steel piles (driven piles) | lot | 15% | 10% | 25% | Gabion retaining wall | cum | 15% | 10% | 25% | [7 empty] | Concrete mixture/ratio shall be class A. |  | - |  |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [11 empty] | 1250kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% | PVC conduits and fittings shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a. Contractor shall provide, install and erect concrete/steel pole or transformer pad. b. Contractor shall comply with the approved design provided by the local electric service provider. | Adapter and locknut shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[11 empty] | Concrete on retaining wall column | cu.m | 15% | 10% | 25% | [5 empty] | Decorative metal | lot | 15% | 10% | 25% | Toilet cabinet (undercounter) | set/s | 15% | 10% | 25% | Selective restoration of roofing | lot | 15% | 10% | 25% | Bi-folding metal door | set/s | 15% | 10% | 25% | Exterior painting (metal components) | lot | 15% | 10% | 25% | Signs and Paraphernalia - "Open/Closed" | set/s | 15% | 10% | 25% | Scent sprayer (automatic, wall-mounted, battery operated) | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, mixer handle, hose spout) | set/s | 15% | 10% | 25% | 150mmØ flexible duct (exhaust) | lm | 15% | 10% | 25% | Unitized Cabinet (1000 x 1850 x 300) | set/s | 15% | 10% | 25% | 20mmØ PVC service entrance cap | pc/s | 15% | 10% | 25% | Auto dialer for fire alarm | set/s | 15% | 10% | 25% | Concrete piles (bored piles) | lot | 15% | 10% | 25% | Riprap | cum | 15% | 10% | 25% | [7 empty] | Concrete mixture/ratio shall be class A. |  | - |  |  |  | a.) All fabricated metal components, metal doors or any metals exposed to weather shall be painted with two (2) coats of zinc oxide. b.) Contractor shall apply applicable putty and ensure that the metal surfaces are smooth and free from holes prior to painting works. c.) Epoxy primer (verify color) shall be applied to ensure that paint will bond to the metal surface. d.) Two (2) coats of glossy epoxy paint (verify color) shall be used for finishing/final coating. | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [11 empty] | 1550kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Contractor must refer to electrical plans for location and specifications. b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, tin plated cooper busbars with insulators, and concrete base platform. c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) No fabrication and installation shall be done without DBP’s proper approval e.) Contractor to ensure first the application of permanent power before installation and fabrication | End bell shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[11 empty] | Concrete on retaining wall column footing | cu.m | 15% | 10% | 25% | [5 empty] | PWD grab-bar | lot | 15% | 10% | 25% | Toilet cabinet (overhead) | set/s | 15% | 10% | 25% | Selective restoration of roofing accessories | lot | 15% | 10% | 25% | Metal louver door (single) | set/s | 15% | 10% | 25% | Exterior painting (perimeter fence) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Teller's Counter No. 1" | set/s | 15% | 10% | 25% | Hand dryer (automatic) | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, double-lever handle, hose spout) | set/s | 15% | 10% | 25% | Exhaust vent (wall mounted) | set/s | 15% | 10% | 25% | Panel "MCB" | lot | 15% | 10% | 25% | 25mmØ PVC service entrance cap | pc/s | 15% | 10% | 25% | Mounting termination, testing, commissioning and programming | lot | 15% | 10% | 25% | Steel piles (bored piles) | lot | 15% | 10% | 25% | Exterior flagpole | lot | 15% | 10% | 25% | [7 empty] | Concrete mixture/ratio shall be class A. |  | a.) Materials shall be 37.5mm stainless steel grab rail on 75mm dia. escutcheon plate with 4 pcs. stainless steel screws and expansion bolt. b.) Refer to fabrication details at DBP standard booklet. |  |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | a.) Hand dryer shall be wall-mounted, automatic with sensor, white plastic finish and can be plugged directly into a wall outlet. b.) Mounting height shall be 1200mm above finish floor line. c.) Design shall be same or similar as to the photo at DBP standard booklet. | [10 empty] | 1875kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | End bell shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | Contractor holds responsibility for mounting termination, testing, commissioning and programming to ensure that every component and system is operational
[11 empty] | Concrete on ramp | cu.m | 15% | 10% | 25% | [5 empty] | Ramp railings | lot | 15% | 10% | 25% | Toilet drawer | set/s | 15% | 10% | 25% | Acrylic barrier (for teller) | set/s | 15% | 10% | 25% | Metal louver door (double) | set/s | 15% | 10% | 25% | Exterior painting (site components) | lot | 15% | 10% | 25% | Signs and Paraphernalia - "Teller's Counter No. 2" | set/s | 15% | 10% | 25% | Water heater | set/s | 0 | 10% | 10% | [5 empty] | Above-counter faucet (stainless, double-mixer handle, hose spout) | set/s | 15% | 10% | 25% | Exhaust vent (roof mounted) | set/s | 15% | 10% | 25% | Panel "MCB1" | lot | 15% | 10% | 25% | 32mmØ PVC service entrance cap | pc/s | 15% | 10% | 25% | Burglar alarm control panel | set/s | 15% | 10% | 25% | Caissons | lot | 15% | 10% | 25% | Concrete PWD ramp | lot | 15% | 10% | 25% | [7 empty] | Concrete mixture/ratio shall be class A. |  | a.) Materials shall be 37.5mm stainless steel pipe railing on 6mm thick stainless steel base plate with 12mm dia. stainless steel bolts and expansion shield. b.) Refer to fabrication details at DBP standard booklet |  | a.) Barrier dimensions: 0.9m height, varrying length b.) Barrier shall be 1/4" thick clear acrylic sheet on 1cm white powder coated aluminum channel. c.) Inclusive of 10" x 3" pigeon hole with sliding enclosure. d.) Glass silicone sealant must be clear. |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [11 empty] | 2250kVA 60hz 230V 3-phase generator set (outdoor type) | lot | 15% | 10% | 25% |  | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | End bell shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[11 empty] | Concrete on parapet wall beam | cu.m | 15% | 10% | 25% | [5 empty] | Aluminum composite panels (ACP) | sqm | 15% | 10% | 25% | Wooden shelves | set/s | 15% | 10% | 25% | Acrylic barrier (for NAC) | set/s | 15% | 10% | 25% | Metal grill door (swing type) | set/s | 15% | 10% | 25% | Interior painting (walls) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Teller's Counter No. 3" | set/s | 15% | 10% | 25% | TV bracket | set/s | 0 | 10% | 10% | [5 empty] | Hand bidet (stainless steel finish) | set/s | 15% | 10% | 25% | Tapping to existing exhaust system | lot | 15% | 10% | 25% | Panel "MCB1b" | lot | 15% | 10% | 25% | 40mmØ PVC service entrance cap | pc/s | 15% | 10% | 25% | Siren with strobelights | set/s | 15% | 10% | 25% | Foundation anchors | lot | 15% | 10% | 25% | Stainless steel railings | lot | 15% | 10% | 25% | [7 empty] | Concrete mixture/ratio shall be class A. |  |  |  | a.) Barrier dimensions: 1.25m height, varrying length b.) Barrier shall be 1/4" thick clear acrylic sheet on 1cm white powder coated aluminum channel. c.) Inclusive of 10" x 3" pigeon hole with sliding enclosure. d.) Glass silicone sealant must be clear. | a.) Grille door dimensions: 900mm width x 2100mm length/height b.) Materials shall be 12mm dia. vertical solid bars spaced at every 100mm and 6mm x 20mm horizontal punched flat bars frame. c.) Other accessories such as fabricated hinges (3 sets) and double deadbolt on metal housing and shall be included. d.) Refer to schedule of doors at DBP standard booklet. | a.) All masonry/concrete walls shall be applied with masonry neuralizer with 1:16 neuralizer-water ratio. b.) Contractor shall apply masonry putty and ensure that the wall surface is smooth prior to painting. c.) Primer acrylic latex paint (color: white) shall be applied to ensure that paint will bond to the wall surface. d.) Two (2) coats of semi-gloss acrylic latex paint (color: white) shall be used for finishing/final coating. | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | Bidet shall be in stainless steel finish and at least 1m long. | [8 empty] | 1kVA 60hz 230V single phase UPS | set/s | 15% | 10% | 25% |  | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | End bell shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system. | a.) Capacity KVA rating: 1,000 VA b.) AC Operating Voltage Range: 208 to 240V c.) Frequency Range: 60Hz ±5% d.) AC Input Voltage: 220 to 240V e.) AC Output Voltage: 220 to 240V f.) Output Receptacles / Port: ≥2 (min.) g.) Power Factor: 0.9 - 1 h.) Output Wave Form: Sine wave / Pure sine wave i.) Display (LCD Panel): General and other information (battery, power status, etc.) j.) Features: Protection (≥ 600 joules for surge energy rating, overload, etc.) k.) inclusive of necessary accessories to operate the system.
[21 empty] | ACP framing/support | lot | 15% | 10% | 25% | Wooden shelves (overhead) | set/s | 15% | 10% | 25% | ATM sunshade | set/s | 15% | 10% | 25% | Metal grill door (sliding) | set/s | 15% | 10% | 25% | Interior painting (ceiling) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Teller's Counter No. 4" | set/s | 15% | 10% | 25% | Calendar clock | set/s | 0 | 10% | 10% | [5 empty] | Soap dispenser (wall mounted, push-button type) | set/s | 15% | 10% | 25% | Electric fan (ceiling mounted, orbital type) | set/s | 15% | 10% | 25% | Panel "MCB1c" | lot | 15% | 10% | 25% | 110mmØ PVC service entrance cap | pc/s | 15% | 10% | 25% | Auto dialer for burglar alarm | set/s | 15% | 10% | 25% | Excavation | lot | 15% | 10% | 25% | Concrete electric pole | lot | 15% | 10% | 25% | [11 empty] | a.) Framing shall be made of 45mm dia. stainless steel pipe vertical support with 6mm cover plate bolted on floor and underslab. b.) Panel shall be made of 6mm thk clear solid polycarbonate without line bifocals and clipped using 6mm x 20mm stainless steel clip. c.) Blue sticker (sultan blue 3630-157) shall be attached installed as backing of the panel. d.) DBP logo shall be computer cut-out and laminated. e.) All necessary miscellaneous materials/consumables such as silicon sealant, rivets and bolts shall be included. f.) Verify actual measurements and mounting prior to sunshade fabrication. | a.) Grille door dimensions: 900mm width x 2100mm length/height b.) Materials shall be 12mm dia. vertical solid bars spaced at every 100mm and 6mm x 20mm horizontal punched flat bars frame. c.) Other accessories such as door track (at interior side) and double deadbolt on metal housing and shall be included. d.) Refer to schedule of doors at DBP standard booklet. | a.) All concrete underslab shall be applied with masonry neuralizer with 1:16 neuralizer-water ratio. b.) Contractor shall apply masonry putty and ensure that the wall surface is smooth and free from defects prior to painting. c.) Primer acrylic latex paint (color: white) shall be applied to ensure that paint will bond to the wall surface. d.) Two (2) coats of flat finish acrylic latex paint (color: white) shall be used for finishing/final coating. | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | a.) Clock shall be digital and can be plugged in an outlet. b.) Background shall be black in color. c.) Time, date and day shall be in LED red font. d.) Contractor shall verify mounting height and location. |  | a.) Soap dispenser shall be wall mounted , push-button type and stainless steel finish. b.) Contractor shall verify actual mounting height and location. | [8 empty] | 2kVA 60hz 230V single phase UPS | set/s | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor to install necessary accessories: hanger & support, mouting accessories, switches | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | End bell shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on CHB wall | kg | 15% | 10% | 25% | Selective demolition of wood component | set/s | 15% | 10% | 25% | ATM sunshade (curved) | set/s | 15% | 10% | 25% | Roll-up door | lot | 15% | 10% | 25% | Interior painting (underslab) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Teller's Counter No. 5" | set/s | 15% | 10% | 25% | Rate board | set/s | 0 | 10% | 10% | [5 empty] | Soap dispenser (wall mounted, touchless type) | set/s | 15% | 10% | 25% | Electric fan (wall mounted, orbital type) | set/s | 15% | 10% | 25% | Panel "LPG" | lot | 15% | 10% | 25% | 19.0mm dia IMC pipe (3m/pc) | pc/s | 15% | 10% | 25% | Magnetic door contact | pc/s | 15% | 10% | 25% | Earthfill | cum | 15% | 10% | 25% | Concrete transformer platform | lot | 15% | 10% | 25% | [9 empty] | Refer to structural details at DBP standard booklet for rebar size/s. |  |  |  | a.) All concrete underslab shall be applied with masonry neuralizer with 1:16 neuralizer-water ratio. b.) Contractor shall apply masonry putty and ensure that the wall surface is smooth and free from defects prior to painting. c.) Primer acrylic latex paint (color: white) shall be applied to ensure that paint will bond to the wall surface. d.) Two (2) coats of flat finish acrylic latex paint (color: white) shall be used for finishing/final coating. | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | a.) Soap dispenser shall be wall mounted , touchless type and stainless steel finish. b.) Contractor shall verify actual mounting height and location. | [8 empty] | 3kVA 60hz 230V single phase UPS | set/s | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor to install necessary accessories: hanger & support, mouting accessories, switches | a.) Contractor shall provide NEMA3R gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) No fabrication and installation shall be done without DBP’s proper approval | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system. | a.) Capacity KVA rating: 3,000 VA b.) AC Operating Voltage Range: 208 to 240V c.) Frequency Range: 60Hz ±5% d.) AC Input Voltage: 220 to 240V e.) AC Output Voltage: 220 to 240V f.) Output Receptacles / Port: ≥2 (min.) g.) Power Factor: 0.9 - 1 h.) Output Wave Form: Sine wave / Pure sine wave i.) Display (LCD Panel): General and other information (battery, power status, etc.) j.) Features: Protection (≥ 600 joules for surge energy rating, overload, etc.) k.) inclusive of necessary accessories to operate the system.
[21 empty] | Rebars on slab (on-grade) | kg | 15% | 10% | 25% | Selective restoration of wood component | sqm | 15% | 10% | 25% | Brise soleil | lot | 15% | 10% | 25% | Roll-up door (perforated) | lot | 15% | 10% | 25% | Interior painting (doors and door jamb) | lot | 15% | 10% | 25% | Signs and Paraphernalia - "Teller's Counter No. 6" | set/s | 15% | 10% | 25% | Vanity mirror | set/s | 0 | 10% | 10% | [5 empty] | Soap dispenser (counter mounted, pump type) | set/s | 15% | 10% | 25% | Electric fan (standing type) | set/s | 15% | 10% | 25% | Panel "LP" | lot | 15% | 10% | 25% | 25.4mm dia IMC pipe (3m/pc) | pc/s | 15% | 10% | 25% | Magnetic door contact for exit and entry (recessed type) | pc/s | 15% | 10% | 25% | [5 empty] | Planting irrigation system | lot | 15% | 10% | 25% | [9 empty] | Refer to structural details for rebar size/s. |  |  |  | a.) Contractor shall apply masonry putty and ensure that the door and jamb surface is smooth and free from defects prior to painting. c.) Lacquer primer paint (color: white) shall be applied to ensure that paint will bond to the wall surface. d.) Two (2) coats of duco/high gloss lacquer paint (color: white) shall be used for finishing/final coating. | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | a.) Mirror dimensions: 800mm height x 600mm length x 1/4" thick b.) Mirror shall be frameless and with beveled edges. c.) Contractor shall verify actual mounting height. |  | a.) Soap dispenser shall be counter mounted, with pump head, extension tube and in stainless steel finish. b.) Contractor shall verify actual mounting height and location. | [8 empty] | 4kVA 60hz 230V single phase UPS | set/s | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor to install necessary accessories: hanger & support, mouting accessories, switches | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on slab (elevated) | kg | 15% | 10% | 25% | Teller counter (woodworks/cabinetwork and solid surface countertop) | set/s | 15% | 10% | 25% | Flood testing | lot | 15% | 10% | 25% | PVC door | set/s | 15% | 10% | 25% | Interior painting (cabinet, drawers and other furnishings) | lot | 15% | 10% | 25% | Signs and Paraphernalia - "Teller's Counter No. 7" | set/s | 15% | 10% | 25% | Entrance mat | sqm | 0 | 10% | 10% | [5 empty] | Soap holder (stainless steel finish) | set/s | 15% | 10% | 25% | Electric fan (tower type, bladeless) | set/s | 15% | 10% | 25% | Panel "LP1" | lot | 15% | 10% | 25% | 31.7mm dia IMC pipe (3m/pc) | pc/s | 15% | 10% | 25% | Magnetic door contact for vault door (heavy duty) | pc/s | 15% | 10% | 25% | [5 empty] | Landscaping topsoil | cum | 15% | 10% | 25% | [9 empty] | Refer to structural details for rebar size/s. | a.) Counter dimensions: 1.2m length (minimum) / 1.5m length (maximum) x 1.0m total width/depth x 1.1m total height. b.) Counter shall use 20mm thick marine plywood for substrate, backing, drawers and pull-out keyboard. c.) Countertop finish shall be made of 10mm thick solid surface, color: white. Curve shall have kiln-died tanguile solid wood moulding and edges shall be post-formed. d.) Tabletop shall be matte laminated vinyl finish, color: light gray. e.) Drawer handles shall be cylindrical stainless steel pull. f.) Pull-out keyboard shall have solid edging and extendable drawer guide. g.) Baseboard shall be stainless steel mirror finish. h.) Base must have floor leveller. i.) Accessories such as forms rack, picos tray and rubber mat shall be included. j.) Forms rack shall be made of 4.5mm thick clear acrylic. k.) Picos tray shall be made of 6mm thick clear acrylic. l.) Rubber mat shall have velcrostrip on underside. m.) Refer to fabrication details at DBP standard booklet. | Water leaks shall be observed if it will occur within the seven (7) days flood testing period. |  | a.) Contractor shall apply masonry putty and ensure that the wood surface is smooth and free from defects prior to painting. c.) Lacquer primer paint (color: white) shall be applied to ensure that paint will bond to the wall surface. d.) Two (2) coats of duco/high gloss lacquer paint (color: white) shall be used for finishing/final coating. | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | a.) Mat shall be made of 15mm thick rug pine. b.) Color black c.) Tile edging and floor drain shall be provided (separate item). d.) Refer to tiling layout and details. | [10 empty] | 5kVA 60hz 230V single phase UPS | set/s | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor to install necessary accessories: hanger & support, mouting accessories, switches | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on vault slab (elevated) | kg | 15% | 10% | 25% | NAC counter (woodworks/cabinetwork and solid surface countertop) | set/s | 15% | 10% | 25% | Roof flashing | sqm | 15% | 10% | 25% | Exterior frameless glass door (single) | set/s | 15% | 10% | 25% | Interior painting (metal components) | lot | 15% | 10% | 25% | Signs and Paraphernalia - "Teller's Counter No. 8" | set/s | 15% | 10% | 25% | Slop sink overhead stainless rack | set/s | 0 | 10% | 10% | [5 empty] | Soap bottle holder (stainless steel finish) | set/s | 15% | 10% | 25% | UV air purifier | set/s | 15% | 10% | 25% | Panel "LP1c" | lot | 15% | 10% | 25% | 63.5mm dia IMC pipe (3m/pc) | pc/s | 15% | 10% | 25% | Hold-up buttons | set/s | 15% | 10% | 25% | [5 empty] | Topsoil placement and grading | lot | 15% | 10% | 25% | [9 empty] | Refer to vault details for rebar size/s. | a.) Counter dimensions: 1.2m length (minimum) / 1.5m length (maximum) x 0.9m total width/depth x 0.75m total height. b.) Counter shall use 20mm thick marine plywood for backing/substrate including PVC pull-out keyboard tray. c.) Countertop finish shall be made of 10mm thick solid surface, color: white. Curve shall have kiln-died tanguile solid wood moulding and edges shall be post-formed. d.) Tabletop shall be matte laminated vinyl finish, color: light gray. e.) Baseboard shall be stainless steel mirror finish. f.) Base must have floor leveller. g.) Refer to fabrication details at DBP standard booklet. |  | a.) Door size: 900mm width x 2100mm length/height b.) Shall be made of 12mm thick clear tempered glass panel. c.) Frosted glass sticker shall be provided d.) Refer to schedule of doors at DBP standard booklet. | a.) All fabricated metal components shall be painted with two (2) coats of zinc oxide. b.) Contractor shall apply applicable putty and ensure that the metal surfaces are smooth and free from defects prior to painting works. c.) Epoxy primer (verify color) shall be applied to ensure that paint will bond to the metal surface. d.) Two (2) coats of glossy epoxy paint (verify color) shall be used for finishing/final coating. | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [11 empty] | 6kVA 60hz 230V single phase UPS | set/s | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor to install necessary accessories: hanger & support, mouting accessories, switches | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system. | a.) Capacity KVA rating: 6,000 VA b.) DC Rated voltage: ≥12V c.) DC input range: ≥ 10V d.) AC Operating Voltage Range: 208 to 240V e.) Frequency Range: 60Hz ±5% f.) AC Input Voltage: 220 to 240V g.) AC Output Voltage: 220 to 240V h.) Output Wave Form: Sine wave / Pure sine wave i.) Battery Voltage: ≥1 pcs, 12V 7Ah Battery j.) Operating Temperature: 0 to 40ºC k.) Audible Noise: ≤ 58dBA h.) inclusive of necessary accessories to operate the system.
[21 empty] | Rebars on column | kg | 15% | 10% | 25% | Guard's podium | set/s | 15% | 10% | 25% | Stainless roof gutter | lm | 15% | 10% | 25% | Frameless glass door (double) | set/s | 15% | 10% | 25% | Interior painting (sprinkler pipes) | lot | 15% | 10% | 25% | Signs and Paraphernalia - "Teller's Are Not Allowed Custody of Passbook" (standee) | set/s | 15% | 10% | 25% | [10 empty] | Tissuer holder (wall mounted, stainless steel finish) | set/s | 15% | 10% | 25% | Transfer fan (wall mounted) | set/s | 15% | 10% | 25% | Panel "PPAC" | lot | 15% | 10% | 25% | 101.6mm dia IMC pipe (3m/pc) | pc/s | 15% | 10% | 25% | Foot rail switches | set/s | 15% | 10% | 25% | [5 empty] | Groundcover | lot | 15% | 10% | 25% | [9 empty] | Refer to structural details for rebar size/s. | Refer to fabrication details at DBP standard booklet. |  | a.) Door size: 800mm width x 2100mm length/height (2 sets) b.) Shall be made of 12mm thick clear tempered glass panel. c.) Refer to schedule of doors at DBP standard booklet. |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | a.) Tissue holder shall be wall-mounted (400mm above finish floor line) and in stainless steel finish. b.) Contractor shall verify actual mounting location. | [8 empty] | 7.5kVA 60hz 230V single phase UPS | set/s | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor to install necessary accessories: hanger & support, mouting accessories, switches | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on stiffener column | kg | 15% | 10% | 25% | Forms counter | set/s | 15% | 10% | 25% | Aluminum sheet fascia | sqm | 15% | 10% | 25% | Framed glass door (single) | set/s | 15% | 10% | 25% | Metal stair nosing | lot | 15% | 10% | 25% | Signs and Paraphernalia - "Please Count Your Money Before Leaving" (standee) | set/s | 15% | 10% | 25% | [10 empty] | Tissuer holder (stand-type, stainless steel finish) | set/s | 15% | 10% | 25% | Transfer fan (ceiling mounted) | set/s | 15% | 10% | 25% | Panel "PPAC1a" | lot | 15% | 10% | 25% | 19.0mm dia IMC elbow | pc/s | 15% | 10% | 25% | Money clip | pc/s | 15% | 10% | 25% | [5 empty] | Plants and bulbs | lot | 15% | 10% | 25% | [9 empty] | Refer to structural details at DBP standard booklet for rebar size/s. | a.) Counter shall be made of 20mm thick marine plywood. b.) Forms shelves and countertop shall be made of 12.5mm thick tempered glass with polished edges. c.) Waste bin door shall have push type lock and concealed hinges. d.) Baseboard shall be stainless steel mirror finish. e.) Base must have metal gliders. f.) Refer to fabrication details at DBP standard booklet. |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [11 empty] | 10kVA 60hz 230V single phase UPS | set/s | 15% | 10% | 25% | a.) Contractor must refer to mechanical plans for location and specifications. b.) Contractor to install necessary accessories: hanger & support, mouting accessories, switches | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Elbow shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system. | a.) Capacity KVA rating: 10,000 VA b.) DC Rated voltage: ≥12V c.) DC input range: ≥ 10V d.) AC Operating Voltage Range: 208 to 240V e.) Frequency Range: 60Hz ±5% f.) AC Input Voltage: 220 to 240V g.) AC Output Voltage: 220 to 240V h.) Output Wave Form: Sine wave / Pure sine wave i.) Battery Voltage: ≥1 pcs, 12V 7Ah Battery j.) Operating Temperature: 0 to 40ºC k.) Audible Noise: ≤ 58dBA h.) inclusive of necessary accessories to operate the system.
[21 empty] | Rebars on vault column | kg | 15% | 10% | 25% | Server counter | set/s | 15% | 10% | 25% | Drip mould | lm | 15% | 10% | 25% | Framed glass door (double) | set/s | 15% | 10% | 25% | Stainless steel tile trim (L-profile) | lot | 15% | 10% | 25% | Signs and Paraphernalia - "Clearing Cut-off Time" (standee) | set/s | 15% | 10% | 25% | [10 empty] | Towel holder (single, stainless steel finish) | set/s | 15% | 10% | 25% | Dome type exhaust air grille | set/s | 15% | 10% | 25% | Panel "PPAC1b" | lot | 15% | 10% | 25% | 25.4mm dia IMC elbow | pc/s | 15% | 10% | 25% | Vibration contact | set/s | 15% | 10% | 25% | [5 empty] | Shrubs | lot | 15% | 10% | 25% | [9 empty] | Refer to vault details for rebar size/s. | a.) Counter dimensions: 1.5m length (maximum) x 0.75m width x 0.75m height. b.) Counter support shall be made 2' x 4" lumber stand and 20mm thick marine plywood side panels. c.) Countertop shall be made of HPL light gray finish on 40mm thick marine plywood with PVC edging to match laminate color. d.) Accessories such as 280mm x 80mm rectangular grommet and PVC pull-out keyboard tray shall be included. e.) Refer to fabrication details at DBP standard booklet. |  |  | a.) Tile trim finish shall be L-profile and in satin stainless steel. b.) All tile end edges and door termination shall have tile trim. c.) Contractor shall verify size depending on tile thickness. | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | a.) Towel holder shall be wall-mounted, single bar/row and in stainless steel finish. b.) Contractor shall verify actual mounting height and location. | [8 empty] | NOTES: |  |  |  |  | a.) Contractor shall provide and install wall mounted 45º downward tilt 150mmØ stainless steel exhaust air grille built-in with mesh for insect screen and stainless steel louver b.) Contractor to install all necessary accessories; hanger and support, and mounting accessories. | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Elbow shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system. | 1.) Contractor shall provide OEM certificate and comply with the standards of ISO 9001, ISO14001. 2.) Contractor shall supply, deliver, test and commision the Generator set compliant with the certification requirements issued by the Bureau of Philippine Standards of Department of Trade and Industry (DTI-BPS) 3.) Contractor to provide and install all necessary pipes, fittings, boxes, cables, hanger, supports, and accessories to operate the generator set. 4.) Contractor shall restore the affected ceiling, wall, floor, etc. during the hauling and installation of the Generator Set. 5.) Contractor to provide the Generator Set a full tank of fuel for testing and commissioning. 6.) Contractor to include the excavation works for conduit installation and Generator Set pad. 7.) Contractor to install all necessary standard mounting accessories. 8.) Contractor shall submit all documents (PTO, DENR, EMB requirements, and PME signed and sealed) and pay all the fees necessary for genset to operate. 9.) No installation shall be without DBP’s proper approval.
[21 empty] | Rebars on column footing | kg | 15% | 10% | 25% | Typing table | set/s | 15% | 10% | 25% | 6" stainless dome strainer | set/s | 15% | 10% | 25% | Vault door | set/s | 15% | 10% | 25% | Stainless steel tile trim (T-profile) | lot | 15% | 10% | 25% | Signs and Paraphernalia - "Priority Lane" (standee) | set/s | 15% | 10% | 25% | [10 empty] | Towel holder (rack type, stainless steel finish) | set/s | 15% | 10% | 25% | [5 empty] | Panel "PPAC1c" | lot | 15% | 10% | 25% | 31.7mm dia IMC elbow | pc/s | 15% | 10% | 25% | Vibration contact (wall mounted) | set/s | 15% | 10% | 25% | [5 empty] | Trees | lot | 15% | 10% | 25% | [9 empty] | Refer to structural details for rebar size/s. | a.) Counter dimensions: 0.55m length x 0.45m width x 0.8m height. b.) Side panels shall be made of 20mm thick marine plywood. c.) Countertop shall be made of HPL light gray finish on 20mm thick marine plywood with PVC edging to match laminate color. d.) Set/s of wheel casters shall be included. e.) Refer to fabrication details at DBP standard booklet. |  | a.) Minimum opening size: 980mm width x 2000mm length/height b.) Minimum door thickness: 365mm c.) Fire rating: two (2) hours maximum d.) Door shall be stainless steel cladded. e.) Locking bolts shall be at 16 pcs. and 38mm diameter (minimum). f.) Other accessories such as ventilator (built-in into frame), time lock (dual combination) and grill day gate shall be included. g.) Refer to schedule of doors at DBP standard booklet. | a.) Tile trim finish shall be T-profile and in satin stainless steel. b.) Profile shall be used to distinguish tile colors. c.) Contractor shall verify size depending on tile thickness. | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [17 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Elbow shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on wall footing | kg | 15% | 10% | 25% | Money counter module | set/s | 15% | 10% | 25% | [5 empty] | Revolving door entrance | set/s | 15% | 10% | 25% | Solid surface countertop | sqm | 15% | 10% | 25% | Signs and Paraphernalia - Reserved for Senior Citizens, PWD and Pregnant Women" | set/s | 15% | 10% | 25% | [10 empty] | Towel holder (ring type, stainless steel finish) | set/s | 15% | 10% | 25% | [5 empty] | Panel "PPUPS" | lot | 15% | 10% | 25% | 63.5mm dia IMC elbow | pc/s | 15% | 10% | 25% | Vibration contact (ceiling mounted) | set/s | 15% | 10% | 25% | [19 empty] | Refer to structural details for rebar size/s. | a.) Counter dimensions: 0.3m length x 0.25m width x 0.75m height. b.) Counter and side panels shall be made of 20mm thick marine plywood. c.) Set/s of wheel casters shall be included. d.) Refer to fabrication details at DBP standard booklet. |  |  | a.) Thickness: 1/2" b.) Finish: white terrazo c.) Provide sample for DBP approval d.) Framing/concrete counter shall be included (separate item) e.) Refer to guardhouse details. | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [17 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Elbow shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on beam | kg | 15% | 10% | 25% | Sand box | set/s | 15% | 10% | 25% | [5 empty] | Automatic door entrance (sliding) | set/s | 15% | 10% | 25% | Selective repainting | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Public Assistance Help Desk" (standee) | set/s | 15% | 10% | 25% | [10 empty] | Clothes hook (single, stainless steel finish) | set/s | 15% | 10% | 25% | [5 empty] | Panel "PPUPS1a" | lot | 15% | 10% | 25% | 101.6mm dia IMC elbow | pc/s | 15% | 10% | 25% | Vibration contact (floor mounted) | set/s | 15% | 10% | 25% | [19 empty] | Refer to structural details for rebar size/s. | a.) Box dimensions: 0.4m length x 0.4m width x 0.6m height. b.) Box and cover shall be made of 20mm thick marine plywood. c.) Cover handle shall be included. d.) Refer to fabrication details at DBP standard booklet. |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | a.) Clothes hook shall be mounted at the interior back side of the toilet door, single hook and in stainless steel finish. b.) Contractor shall verify actual mounting height. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Elbow shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on upstand beam | kg | 15% | 10% | 25% | Poster module | set/s | 15% | 10% | 25% | [5 empty] | Automatic door entrance (swing type) | set/s | 15% | 10% | 25% | Paint stripping/removal | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "New Accounts Section" | set/s | 15% | 10% | 25% | [10 empty] | Grease trap (stainless steel finish) | set/s | 15% | 10% | 25% | [5 empty] | Panel "PPUPS1b" | lot | 15% | 10% | 25% | 19.0mm dia IMC coupling | pc/s | 15% | 10% | 25% | Silent signaling device (LED indicator) | pc/s | 15% | 10% | 25% | [19 empty] | Refer to structural details at DBP standard booklet for rebar size/s. |  |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | a.) Grease trap shall be stainless steel finish. b.) Capacity shall be 8lbs and with 5GPM discharge. c.) Complete set with grease trap interceptor. d.) Outlet shall fit with plumbing pipe. e.) Provide sample photo/s and specifications for DBP approval. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Coupling shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on lintel beam | kg | 15% | 10% | 25% | CCTV cabinet | set/s | 15% | 10% | 25% | [5 empty] | Frameless glasswall (exterior) | sqm | 15% | 10% | 25% | Cellulose fiber glass wool insulation | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Branch Head" | set/s | 15% | 10% | 25% | [10 empty] | Clean-out (4", brass finish) | set/s | 15% | 10% | 25% | [5 empty] | Panel "PPUPS1c" | lot | 15% | 10% | 25% | 25.4mm dia IMC coupling | pc/s | 15% | 10% | 25% | Buzzer with emergency button | set/s | 15% | 10% | 25% | [19 empty] | Refer to structural details at DBP standard booklet for rebar size/s. | a.) Cabinet dimensions: 0.6m length x 0.6m width x 0.8m height. b.) Side panels and cabinet doors shall be made of 20mm thick marine plywood with 2mm wide slats and insect screen. Stainless steel pull, lock and concealed hinges shall be included. c.) Countertop shall be made of HPL light gray finish on 20mm thick marine plywood with PVC edging to match laminate color. d.) Refer to fabrication details at DBP standard booklet. |  | a.) Shall be made of 12mm thick clear tempered glass panel with concealed aluminum clip holder on top and bottom. b.) Refer to schedule of glass panels at architectural plans. c.) Verify actual measurements on site prior to fabrication |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | a.) Clean-out shall be 4" dia. and in brass finish. b.) Refer to clean-out location at plumbing plans. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Coupling shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on bond beam | kg | 15% | 10% | 25% | Flag pole base stand | set/s | 15% | 10% | 25% | [5 empty] | Frameless glasswall (interior) | sqm | 15% | 10% | 25% | Exterior painting (columns) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - Peso-Dollar Exchange Rate Board | set/s | 15% | 10% | 25% | [10 empty] | 100mm dia PVC waste pipe (3m/pc) | pc/s | 15% | 10% | 25% | [5 empty] | Panel "MCB2" | lot | 15% | 10% | 25% | 31.7mm dia IMC coupling | pc/s | 15% | 10% | 25% | Motion detection light | set/s | 15% | 10% | 25% | [19 empty] | Refer to structural details at DBP standard booklet for rebar size/s. |  |  | a.) Shall be made of 12mm thick clear tempered glass panel with concealed aluminum clip holder on top and bottom. b.) Refer to schedule of glass panels at architectural plans. c.) Verify actual measurements on site prior to fabrication |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Inserts shall be included. d.) Refer to signage details for design, mounting height and location. |  |  | a.) Color: gray/dark gray b.) Exposed pipes shall be properly labeled. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Coupling shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on vault beam | kg | 15% | 10% | 25% | Wooden pole with base inclusive of flag | set/s | 15% | 10% | 25% | [5 empty] | Framed glasswall (exterior) | sqm | 15% | 10% | 25% | Exterior painting (beams) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Date Board with Inserts" (standee) | set/s | 15% | 10% | 25% | [10 empty] | 100mm dia PVC soil pipe (3m/pc) | pc/s | 15% | 10% | 25% | [5 empty] | Panel "MCB2a" | lot | 15% | 10% | 25% | 63.5mm dia IMC coupling | pc/s | 15% | 10% | 25% | Wired glass break detector (shock sensor) | pc/s | 15% | 10% | 25% | [19 empty] | Refer to vault details for rebar size/s. | a.) Flag base dimesions: 12" length x 12" width" x 12" height with 2" dia. dole b.) DBP logo dimensions: 6" length x 6" width x 1/2" thickness c.) Pole dimensions: 2" dia., height for verification d.) Pole and base material and finish: Wood/Semi-gloss white paint e.) Refer to wood fabrication details for further reference. |  | a.) Shall be made of 12mm thick clear tempered glass panel with concealed aluminum clip holder on top and bottom. b.) Refer to schedule of glass panels at architectural plans. c.) Verify actual measurements on site prior to fabrication |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Inserts shall be included. d.) Refer to signage details for design, mounting height and location. |  |  | a.) Color: black b.) Exposed pipes shall be properly labeled. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Coupling shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on parapet wall | kg | 15% | 10% | 25% | Janitor's closet | set/s | 15% | 10% | 25% | [5 empty] | Framed glasswall (interior) | sqm | 15% | 10% | 25% | Exterior painting (ramp) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Restrooms" (back-to-back printing) | set/s | 15% | 10% | 25% | [10 empty] | 50mm dia PVC vent pipe (3m/pc) | pc/s | 15% | 10% | 25% | [5 empty] | Panel "MCB2b" | lot | 15% | 10% | 25% | 101.6mm dia IMC coupling | pc/s | 15% | 10% | 25% | BAS Computer | set/s | 15% | 10% | 25% | [19 empty] | Refer to structural details for rebar size/s. | a.) Closet shall be made of 20mm thick marine plywood with stainless steel cabinet handles and concealed hinges. b.) Verify actual measurements on site. c.) Refer to fabrication details at architectural plans. |  | a.) Shall be made of 12mm thick clear tempered glass panel with concealed aluminum clip holder on top and bottom. b.) Refer to schedule of glass panels at architectural plans. c.) Verify actual measurements on site prior to fabrication |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | a.) Color: gray/dark gray b.) Exposed pipes shall be properly labeled. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Coupling shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on zocalo | kg | 15% | 10% | 25% | AC enclosure | set/s | 15% | 10% | 25% | [5 empty] | Semi-framed glasswall (exterior) | sqm | 15% | 10% | 25% | Exterior painting (cantilever beam) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Restrooms" (3 icons) | set/s | 15% | 10% | 25% | [10 empty] | 20mm dia PVC cold water line (3m/pc) | pc/s | 15% | 10% | 25% | [5 empty] | Panel "MCB2c" | lot | 15% | 10% | 25% | 19.0mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | 22" LED monitor Full HD Resolution | unit/s | 15% | 10% | 25% | [19 empty] | Refer to structural details for rebar size/s. | a.) Enclosure shall be made of 20mm thick marine plywood. b.) Verify actual measurements on site. c.) Refer to fabrication details at architectural plans. |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | a.) Color: white b.) Exposed pipes shall be properly labeled. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Locknut and bushing shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on canopy | kg | 15% | 10% | 25% | Formworks | lot | 15% | 10% | 25% | [5 empty] | Semi-framed glasswall (interior) | sqm | 15% | 10% | 25% | Interior painting (columns) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Emergency Exit" (back-to-back printing) | set/s | 15% | 10% | 25% | [10 empty] | 20mm dia PPR cold water line (4m/pc) | pc/s | 15% | 10% | 25% | [5 empty] | Panel "LP2" | lot | 15% | 10% | 25% | 25.4mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | UPS 625VA | unit/s | 15% | 10% | 25% | [19 empty] | Refer to structural details for rebar size/s. | Maximum re-use of formworks shall be: 7 uses/repetition for 12mm thick plywood and 20 for uses/repetition for 18mm thick plywood |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | a.) Color: white b.) Exposed pipes shall be properly labeled. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Locknut and bushing shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on platform | kg | 15% | 10% | 25% | Vault wooden cabinet (full height, double lock) | set/s | 15% | 10% | 25% | [5 empty] | Door knob (orbit type, keyed) | set/s | 15% | 10% | 25% | Interior painting (beams) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Not an Exit" | set/s | 15% | 10% | 25% | [10 empty] | 15mm dia PVC cold water line (3m/pc) | pc/s | 15% | 10% | 25% | [5 empty] | Panel "LP2a" | lot | 15% | 10% | 25% | 31.7mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | Finger print and proximity reader | set/s | 15% | 10% | 25% | [19 empty] | Refer to structural details for rebar size/s. | a.) Material shall be 20mm thick marine plywood with solid edging for partition, shelves and swing-out cabinet doors. b.) Accessories such as concealed pneumatic cabinet hinges, stainless cabinet handles and double lock shall be included. c.) All necessary mounting support, frame or backing shall be included. d.) Refer to fabrication details at DBP standard booklet. |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | a.) Color: white b.) Exposed pipes shall be properly labeled. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Locknut and bushing shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on counter (lavatory) | kg | 15% | 10% | 25% | Picos tray | set/s | 15% | 10% | 25% | [5 empty] | Door knob (orbit type, keyless) | set/s | 15% | 10% | 25% | Ceramic tiles (slop sink) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Please Conserve Water" | set/s | 15% | 10% | 25% | [10 empty] | 15mm dia PPR cold water line (4m/pc) | pc/s | 15% | 10% | 25% | [5 empty] | Panel "LP2b" | lot | 15% | 10% | 25% | 63.5mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | Single door magnetic lock | set/s | 15% | 10% | 25% | [19 empty] | Refer to structural details at DBP standard booklet for rebar size/s. | a.) Picos tray shall be made of 6mm thk clear acrylic sheet b.) Refer to picos tray design and dimensions on booklet |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | a.) Color: white b.) Exposed pipes shall be properly labeled. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Locknut and bushing shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on counter (kitchen sink) | kg | 15% | 10% | 25% | Rubber mat | set/s | 15% | 10% | 25% | [5 empty] | Door knob (lever type, keyed) | set/s | 15% | 10% | 25% | Acoustic board ceiling (600mm x 600mm) including runner system | sqm | 15% | 10% | 25% | Signs and Paraphernalia - "Turn Off Lights When Not In Use" | set/s | 15% | 10% | 25% | [10 empty] | 4" dia downspout (3m/pc) | pc/s | 15% | 10% | 25% | [5 empty] | Panel "LP2c" | lot | 15% | 10% | 25% | 101.6mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | LZ Bracket | lot | 15% | 10% | 25% | [19 empty] | Refer to structural details at DBP standard booklet for rebar size/s. | a.) Provide rubber mat sample for DBP approval; preferred color: black b.) Velcro strap underneath rubber mat shall be provided |  | a.) Door knob shall be lever type (keyed) and in satin stainless finish. b.) Keys shall be turned-over to DBP upon completion of works. c.) Refer to schedule of doors at DBP standard booklet for mounting height and distance from edge. | a.) Acoustic board size: 600mm length x 600mm width x 10mm thickness b.) Acoustic board shall be fine fissured, lay-in type. c.) Runner system shall be galvanized iron coated and baked white finish including hanger rod and fixed bracket/steel angle attachments. d.) Refer to ceiling plan at architectural plans. | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [17 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Locknut and bushing shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Rebars on stairs | kg | 15% | 10% | 25% | Forms rack | set/s | 15% | 10% | 25% | [5 empty] | Door knob (lever type, keyless) | set/s | 15% | 10% | 25% | Exterior painting (retaining wall) | sqm | 15% | 10% | 25% | Signs and Paraphernalia - Back Office Poster Case | set/s | 15% | 10% | 25% | [10 empty] | 5" dia downspout (3m/pc) | pc/s | 15% | 10% | 25% | [5 empty] | Panel "PP" | lot | 15% | 10% | 25% | 19.0mm dia EMT pipe (3m/pc) | pc/s | 15% | 10% | 25% | U Bracket | pc/s | 15% | 10% | 25% | [19 empty] | Refer to structural details at DBP standard booklet for rebar size/s. | a.) Forms rack shall be made of 4.5mm thk clear acrylic sheet b.) Refer to forms rack design and dimensions on booklet |  | a.) Door knob shall be lever type (keyless) and in satin stainless finish. b.) Keys shall be turned-over to DBP upon completion of works. c.) Refer to schedule of doors at DBP standard booklet for mounting height. |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [17 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Tie wires | kg | 15% | 10% | 25% | PVC keyboard tray | set/s | 15% | 10% | 25% | [5 empty] | Door knob (electronic push button) | set/s | 15% | 10% | 25% | Laminated vinyl finish - white board | sqm | 15% | 10% | 25% | Signs and Paraphernalia - Evacuation Plan | set/s | 15% | 10% | 25% | [10 empty] | 6" dia downspout (3m/pc) | pc/s | 15% | 10% | 25% | [5 empty] | Panel "PP1" | lot | 15% | 10% | 25% | 25.4mm dia EMT pipe (3m/pc) | pc/s | 15% | 10% | 25% | Exit Button | set/s | 15% | 10% | 25% | [19 empty] | Shall be gauge #16 galvanized iron | a.) Keyboard tray shall be made of PVC; color: black b.) Keyboard tray shall be pull-out and installed underneath the countertop c.) Metal track and mounting support shall be included |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [17 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Vault metal components | lot | 15% | 10% | 25% | [10 empty] | Mortise lock | set/s | 15% | 10% | 25% | ACP ceiling | sqm | 15% | 10% | 25% | [15 empty] | 18" dia reinforced concrete pipe (drainage system) | lm | 15% | 10% | 25% | [5 empty] | Panel "PP2" | lot | 15% | 10% | 25% | 31.7mm dia EMT pipe (3m/pc) | pc/s | 15% | 10% | 25% | 12V/3A power supply with back-up battery | set/s | 15% | 10% | 25% | [19 empty] | Refer to vault details for rebar size/s. |  |  |  |  | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. | [17 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Selective demolition of metal component | lot | 15% | 10% | 25% | [10 empty] | Barrel bolt | set/s | 15% | 10% | 25% | Ficem board parapet wall - double wall | sqm | 15% | 10% | 25% | [15 empty] | Concrete catch basin with cover | set/s | 15% | 10% | 25% | [5 empty] | Panel "PP2b" | lot | 15% | 10% | 25% | 19.0mm dia EMT elbow | pc/s | 15% | 10% | 25% | Proximity card | pc/s | 15% | 10% | 25% | [42 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Elbow shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Selective restoration of metal component | lot | 15% | 10% | 25% | [10 empty] | Door latch | set/s | 15% | 10% | 25% | Pebble washout finish | sqm | 15% | 10% | 25% | [15 empty] | Area drain with steel grating | set/s | 15% | 10% | 25% | [5 empty] | Panel "PPAC" | lot | 15% | 10% | 25% | 25.4mm dia EMT elbow | pc/s | 15% | 10% | 25% | 5MP CCTV camera (bullet type) | set/s | 15% | 10% | 25% | [23 empty] | a.) Thickness: 1" b.) Pebble size: #5 c.) Pebble color: Contractor to provide sample for DBP approval. d.) Grout color: to match with pebble color e.) Refer to ramp layout. | [18 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Elbow shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Ferro scanning | lot | 15% | 10% | 25% | [10 empty] | Dead bolt | set/s | 15% | 10% | 25% | Epoxy paint finish | sqm | 15% | 10% | 25% | [15 empty] | Fittings | lot | 15% | 10% | 25% | [5 empty] | Panel "PPAC1" | lot | 15% | 10% | 25% | 31.7mm dia EMT elbow | pc/s | 15% | 10% | 25% | 5MP CCTV camera (fish eye type) | set/s | 15% | 10% | 25% | [19 empty] | Contractor shall verify the concrete areas/portions that will be scanned and mapped. | [7 empty] | All necessary fittings to complete the plumbing works shall be included. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Elbow shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Fabricated window grilles | lot | 15% | 10% | 25% | [10 empty] | Roller latch | set/s | 15% | 10% | 25% | [20 empty] | Consumables | lot | 0% | 10% | 10% | [5 empty] | Panel "PPAC2b" | lot | 15% | 10% | 25% | 19.0mm dia EMT coupling and connector (set screw type) | set/s | 15% | 10% | 25% | 5MP CCTV camera (dome type) | set/s | 15% | 10% | 25% | [24 empty] | a.) Signage shall be made of 1/4" thick clear acrylic with print on back side b.) Signage shall be mounted using industrial grade double-sided tape. c.) Refer to signage details for design, mounting height and location. |  |  | All necessary consumables to complete the plumbing works shall be included. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Coupling and connector shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Rebars on footing tie beam | kg | 15% | 10% | 25% | [10 empty] | Spring bolt | set/s | 15% | 10% | 25% | [20 empty] | Hangers and supports | lot | 15% | 10% | 25% | [5 empty] | Panel "PPAC2c" | lot | 15% | 10% | 25% | 25.4mm dia EMT coupling and connector (set screw type) | set/s | 15% | 10% | 25% | 5MP CCTV camera (pan-tilt-zoom type) | set/s | 15% | 10% | 25% | [22 empty] | a.) Spring loaded bolt shall be push-type and in satin stainless finish. b.) Bolt shall be placed on interior side of door. c.) Refer to schedule of doors at DBP standard booklet for mounting. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Coupling and connector shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Rebars on parapet wall column | kg | 15% | 10% | 25% | [10 empty] | Finger pull bar/handle | set/s | 15% | 10% | 25% | [20 empty] | Leak test | lot | 15% | 10% | 25% | [5 empty] | Panel "PPUPS2" | lot | 15% | 10% | 25% | 31.7mm dia EMT coupling and connector (set screw type) | set/s | 15% | 10% | 25% | 16 channel 32" monitor | set/s | 15% | 10% | 25% | [22 empty] | a.) Finger pull handle shall be in satin stainless finish or white powder coated finish and placed on door frame edge. b.) Refer to schedule of doors at DBP standard booklet for mounting. |  |  |  |  | - | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Coupling and connector shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Rebars on retaining wall footing | kg | 15% | 10% | 25% | [10 empty] | Door closer (pneumatic) | set/s | 15% | 10% | 25% | [20 empty] | Pressure test | lot | 15% | 10% | 25% | [5 empty] | Panel "PPUPS2a" | lot | 15% | 10% | 25% | 19.0mm dia EMT coupling and connector (compression type) | set/s | 15% | 10% | 25% | 24 channel 32" monitor | set/s | 15% | 10% | 25% | [22 empty] | Door closer shall be pneumatic, surface mounted and in satin stainless finish. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Coupling and connector shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Rebars on parapet wall beam | kg | 15% | 10% | 25% | [10 empty] | Door closer (concealed) | set/s | 15% | 10% | 25% | [20 empty] | Tapping to main line | lot | 15% | 10% | 25% | [5 empty] | Panel "PPUPS2b" | lot | 15% | 10% | 25% | 25.4mm dia EMT coupling and connector (compression type) | set/s | 15% | 10% | 25% | 32-channel 32" monitor | set/s | 15% | 10% | 25% | [42 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Coupling and connector shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Rebars on ramp | kg | 15% | 10% | 25% | [10 empty] | Door stopper (floor mounted) | set/s | 15% | 10% | 25% | [20 empty] | Tapping to septic vault | lot | 15% | 10% | 25% | [5 empty] | Panel "PPUPS2c" | lot | 15% | 10% | 25% | 31.7mm dia EMT coupling and connector (compression type) | set/s | 15% | 10% | 25% | 16 channel 22" monitor | set/s | 15% | 10% | 25% | [19 empty] | Refer to ramp details for rebar size/s. |  |  | Door stopper shall be magnetic, wall-mounted and in satin stainless finish. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Coupling and connector shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Rebars on retaining wall column | kg | 15% | 10% | 25% | [10 empty] | Door stopper (wall mounted) | set/s | 15% | 10% | 25% | [20 empty] | Tapping to storm drainage | lot | 15% | 10% | 25% | [5 empty] | Panel "MCB3" | lot | 15% | 10% | 25% | 32mm dia service entrance cap | pc/s | 15% | 10% | 25% | 24 channel 22" monitor | set/s | 15% | 10% | 25% | [22 empty] | Door stopper shall be magnetic, floor-mounted and in satin stainless finish. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Service entrance cap shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Stairs railing | kg | 15% | 10% | 25% | [10 empty] | Stainless steel door handle - H-type (for glass door) | set/s | 15% | 10% | 25% | [20 empty] | Septic vault | lot | 15% | 10% | 25% | [5 empty] | Panel "MCB3a" | lot | 15% | 10% | 25% | 63mm dia service entrance cap | pc/s | 15% | 10% | 25% | 32 channel 22" monitor | set/s | 15% | 10% | 25% | [22 empty] | a.) Door handle shall be 1500mm long, at least 32mm dia, H-type and in polished stainless steel finish. b.) Refer to schedule of doors at DBP standard booklet for mounting height. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Service entrance cap shall be hot-dip galvanized steel material. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Ceiling grilles | kg | 15% | 10% | 25% | [10 empty] | Stainless steel door handle - C-type (for wooden door) | set/s | 15% | 10% | 25% | [20 empty] | Water cistern | lot | 15% | 10% | 25% | [5 empty] | Panel "MCB3b" | lot | 15% | 10% | 25% | Grounding rod (3/4" x 3m) | pc/s | 15% | 10% | 25% | 16 channel network video recorder with 4nos 8TB internal hard drive | set/s | 15% | 10% | 25% | [19 empty] | Ceiling grilles shall be made of 12mm dia. round bar spaced 200mm both ways, fully-welded on every intersection/connection and mounted on existing roof trusses |  |  | a.) Door handle shall be at least 300mm long, C-type and in polished stainless steel finish. b.) Refer to schedule of doors at DBP standard booklet for mounting height. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Grounding rod shall be 3/4" diam x 3m long copper rod. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Overhead steel plate | sht/s | 15% | 10% | 25% | [10 empty] | Stainless steel door handle - pull ring (for wooden door) | set/s | 15% | 10% | 25% | [20 empty] | Water tank | lot | 15% | 10% | 25% | [5 empty] | Panel "MCB3c" | lot | 15% | 10% | 25% | Grounding clamp | pc/s | 15% | 10% | 25% | 32 channel network video recorder with 4nos 8TB internal hard drive | set/s | 15% | 10% | 25% | [19 empty] | 6mm thk. MS plate underside of new concrete slab (top) |  |  | a.) Door handle shall be in polished stainless steel finish. b.) Refer to schedule of doors at DBP standard booklet for mounting height. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Grounding clamp shall be copper plated | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Slab steel plate | sht/s | 15% | 10% | 25% | [10 empty] | Patch fittings | set/s | 15% | 10% | 25% | [20 empty] | Water pump | lot | 15% | 10% | 25% | [5 empty] | Panel "LP3" | lot | 15% | 10% | 25% | Grounding bus bar | pc/s | 15% | 10% | 25% | 32 channel network video recorder with 5nos 8TB internal hard drive | set/s | 15% | 10% | 25% | [19 empty] | 10mm thk. MS plate on concrete floor slab (bottom) |  |  | a.) Patch fittings shall fit with 10-12mm thick glass panels. b.) Patch fittings complete set shall consist of self-closing floor hinges, patch lock, top patch and bottom patch. c.) Patch fittings shall be in satin stainless steel finish. d.) Contractor shall verify type of overhead patch to be used based on actual site conditions. d.) Refer to schedule of doors at DBP standard booklet. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Grounding clamp shall be copper material | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Wall plate | sht/s | 15% | 10% | 25% | [10 empty] | Frameless glass door mid-lock | set/s | 15% | 10% | 25% | [20 empty] | Gate valve | set/s | 15% | 10% | 25% | [5 empty] | Panel "LP3a" | lot | 15% | 10% | 25% | Hanger and support | lot | 15% | 10% | 25% | Network attached storage (NAS)''' | set/s | 15% | 10% | 25% | [19 empty] | 6mm thk. MS plate between two (2) CHB walls |  |  | a.) Mid-lock shall be applicable for frameless glass door, double lock and in stainless steel finish. b.) Refer to schedule of doors at DBP standard booklet. |  |  |  |  | a.) Size: 3/4" dia. b.) Type: gate valve c.) Material: brass d.) Refer to plumbing plans for the layout. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Hanger rod shall be 6mm dia. bar with expansion shield and bolted on underslab. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Bended plate perimeter channel | sht/s | 15% | 10% | 25% | [10 empty] | Stainless steel door hinges (loose pin) | set/s | 15% | 10% | 25% | [20 empty] | Accessories (stainless) | lot | 15% | 10% | 25% | [5 empty] | Panel "LP3b" | lot | 15% | 10% | 25% | Consumables (tape, tagging, PVC cement and accessories) | lot | 0% | 10% | 10% | 8TB Back-up external hard drive with attached storage | set/s | 15% | 10% | 25% | [19 empty] | [ 8 x 11.5 steel channel |  |  | a.) Hinge dimensions: 3.5" x 3.5". b.) Hinge shall be loose pin type (4 holes) and in satin stainless finish. c.) Four (4) set/s shall be provided for wooden door/s. d.) Refer to schedule of doors at DBP standard booklet. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | All necessary consumables to complete the electrical works shall be included. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Ceiling steel channel | pc/s | 15% | 10% | 25% | [10 empty] | Stainless steel door hinges (concealed) | set/s | 15% | 10% | 25% | [20 empty] | Check valve | set/s | 15% | 10% | 25% | [5 empty] | Panel "LP3c" | lot | 15% | 10% | 25% | Junction box with cover (ga#16) | set/s | 15% | 10% | 25% | Network attached storage (NAS)'' | set/s | 15% | 10% | 25% | [19 empty] | [ 8 x 11.5 steel channel |  |  | a.) Hinge load capacity: at least 40kg b.) Hinge shall be concealed type and in satin stainless finish . c.) Four (4) set/s shall be provided for concealed/secret door/s. d.) Refer to schedule of doors at DBP standard booklet. |  |  |  |  | a.) Size: 1" dia. b.) Type: check valve c.) Material: brass d.) Refer to plumbing plans for the layout. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Junction box dimensions: 4" x 4" (GA#16) b.) Junction box deep type with cover and shall be made of galvanized iron. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Dowel for vault door | pc/s | 15% | 10% | 25% | [10 empty] | Stainless steel door hinges (double action) | set/s | 15% | 10% | 25% | [20 empty] | Wall vent | set/s | 15% | 10% | 25% | [5 empty] | Panel "PP3" | lot | 15% | 10% | 25% | Utility box (ga#16) | set/s | 15% | 10% | 25% | Back-up hard drive (60 days real-time retention period inclusive of back-up recorder if applicable)'' | set/s | 15% | 10% | 25% | [19 empty] | 16mm dia x 400mm long dowel bars |  |  | a.) Hinge dimensions: 3.5" x 3.5". b.) Hinge shall be double action spring loaded type and in satin stainless finish. c.) Three (3) set/s shall be provided for low height door/s. d.) Refer to schedule of doors at DBP standard booklet. |  |  |  |  | a.) Mounting: through wall b.) Size: applicable to 50mm dia. pipe c.) Material: stainless d.) Screen shall be included. e) Wallhole shall be properly sealed. g.) Refer to plumbing plans for the layout. | [14 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Utility box dimensions: 4" x 2" (GA#16) b.) Utility box deep type and shall be made of galvanized iron. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Dynabolt | pc/s | 15% | 10% | 25% | [10 empty] | Steel casement window | set/s | 15% | 10% | 25% | [30 empty] | Panel "PP3a" | lot | 15% | 10% | 25% | Pullbox (ga#16) | set/s | 15% | 10% | 25% | Network attached storage (NAS)' | set/s | 15% | 10% | 25% | [19 empty] | Dia 12 x 117mm anchor bolt | [22 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Pullbox dimensions: 24"x 24" x 16" (GA#16) b.) Pullbox material shall be made of galvanized iron. | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[21 empty] | Expansion bolt | pc/s | 15% | 10% | 25% | [10 empty] | Sliding window (aluminum framed) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PP3b" | lot | 15% | 10% | 25% | Wire gutter | pc/s | 15% | 10% | 25% | Back-up hard drive (60 days real-time retention period inclusive of back-up recorder if applicable)' | set/s | 15% | 10% | 25% | [19 empty] | 12mm dia x 3" long ordinary expansion bolt with expansion shield flat head sunken type | [22 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Wire gutter deep type and shall be made of galvanized iron.
[21 empty] | Anchor bolt | pc/s | 15% | 10% | 25% | [10 empty] | Sliding window (wooden framed) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PP3c" | lot | 15% | 10% | 25% | Duplex data port outlet (RJ45) | set/s | 15% | 10% | 25% | Testing and commissioning | lot | 15% | 10% | 25% | [19 empty] | Dia 12 x 117mm anchor bolt | [22 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Duplex data outlet shall be compatible for CAT6 UTP cable | Contractor shall holds responsibilities for mounting termination, testing and commissioning and programming to ensure that every component and system is operational
[21 empty] | Injection mortar | pc/s | 15% | 10% | 25% | [10 empty] | Sliding window (uPVC framed) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PPAC3" | lot | 15% | 10% | 25% | Duplex voice port outlet (RJ11) | set/s | 15% | 10% | 25% | 9U CCTV Cabinet (wall mounted) | set/s | 15% | 10% | 25% | [19 empty] | Hybrid adhesive mortar designed for anchoring applications in non-cracked concrete | [22 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | Duplex voice outlet shall be compatible for CAT6 UTP cable | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Welding works | lot | 15% | 10% | 25% | [10 empty] | Awning window (aluminum framed) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PPAC3a" | lot | 15% | 10% | 25% | Data terminal cabinet (960mm H x 550mm W x 580mm D) | lot | 15% | 10% | 25% | POE Switch | set/s | 15% | 10% | 25% | [19 empty] | a.) All welding materials and consumables shall be included b.) Welding surface shall be cleaned prior to welding works c.) All connections/joints shall be fully-welded d.) Welder shall secure qualification certificate/s | [22 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Framing & paneling: GA#16 b.) 19" standard opening c.) Plexiglass front door with lock d.) Detachable exhaust side panel with lock e.) Fixed type back panel f.) Black powder coated g.) Inclusive of 2-pcs exhaust fan at the top panel, 2-pcs ventilating fan at the bottom panel, cagenut, screw, and other installation accessories | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system.
[21 empty] | Signage framing/support | lot | 15% | 10% | 25% | [10 empty] | Awning window (wooden framed) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PPAC3b" | lot | 15% | 10% | 25% | Horizontal cable manager | set/s | 15% | 10% | 25% | RS232 Cable | m | 15% | 10% | 25% | [19 empty] | a.) Signage framing shall be made of 2" x 2" angle bar b.) Sufficient bracing shall be provided c.) Connections shall be fully-welded d.) Framing shall be painted with two (2) coats of red-oxide e.) Final coating shall match the roof's existing color f.) Provide framing shop drawing for DBP approval | [22 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Contractor to provide and install Unplasticized Polyvinyl Chloride (uPVC) horizontal cable manager fit for DTC
[21 empty] | Angle bar on upstand beam | kg | 15% | 10% | 25% | [10 empty] | Awning window (uPVC framed) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PPAC3c" | lot | 15% | 10% | 25% | Rack shelves | set/s | 15% | 10% | 25% | #12 AWG stranded THHN wire | m | 15% | 10% | 25% | [19 empty] | Refer to upstand beam details for angle bar size/s. | [22 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[36 empty] | Fixed glass window (aluminum framed) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PPUPS3" | lot | 15% | 10% | 25% | Powerstrip 6-convenience outlet for data cabinet | set/s | 15% | 10% | 25% | #16 2C AWG stranded TF wire | m | 15% | 10% | 25% | [42 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[36 empty] | Fixed glass window (wooden framed) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PPUPS3a" | lot | 15% | 10% | 25% | 24 port patch panel | set/s | 15% | 10% | 25% | #22 2C AWG stranded TF wire | m | 15% | 10% | 25% | [42 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Lan Category: Cat6 b.) Number of Ports: 24 c.) Interface Type: RJ45 d.) Shield Type: UTP
[36 empty] | Fixed glass window (frameless) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PPUPS3b" | lot | 15% | 10% | 25% | 48-port manageable LAN switch | set/s | 15% | 10% | 25% | ½" Ø flexible metal conduit | m | 15% | 10% | 25% | [42 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | LAN switch shall refer to DBP DataCom plan
[36 empty] | Swing window (aluminum framed) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PPUPS3c" | lot | 15% | 10% | 25% | Telephone terminal cabinet | lot | 15% | 10% | 25% | ½" Ø straight connector | pc/s | 15% | 10% | 25% | [42 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Protection: NEMA-1 b.) Sheet metal: G.I SHEET c.) Gauge #: Gauge 16 d.) Finish: Powder-coated e.) Color: Gray f.) Dimensions (HxWxD): 600mm x 400mm x 200mm
[36 empty] | Swing window (wooden framed) | set/s | 15% | 10% | 25% | [30 empty] | Panel "MCB4" | lot | 15% | 10% | 25% | Service telephone terminal cabinet with grills and padlock | lot | 15% | 10% | 25% | ½" Ø angle connector | pc/s | 15% | 10% | 25% | [42 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Protection: NEMA-3R and enclosed in steel grills w/ padlock & key b.) Sheet metal: G.I. Sheet c.) Gauge #: Gauge 12-14 d.) Finish: Powder-coated e.) Color: Gray f.) Dimensions (HxWxD): 400mm x 400mm x 200mm
[36 empty] | Swing window (uPVC framed) | set/s | 15% | 10% | 25% | [30 empty] | Panel "MCB4a" | lot | 15% | 10% | 25% | Krone module/10 pairs | set/s | 15% | 10% | 25% | ½" Ø EMT conduit (3m/pc) | pc/s | 15% | 10% | 25% | [42 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Conductor Diameter of connectable wires (2 wires per contact): 0.40 to 0.63mm b.) Conductor Diameter of connectable wires (1 wire per contact): 0.63 to 0.8mm; AWG 22 to AWG 26 c.) Insulation diamter of Connectable wires: 0.7 to 1.6mm d.) Connection frequency: >200 times e.) Test access plug in cycles: >250 f.) Contact resistance: <2.5m ohms g.) Insulation resistance: >50,000 Mega ohms h.) Dielectric strength: 2KV rms i.) Impulse current: 5kA (8/20 micro sec) j.) Current carrying capacity: 2A
[36 empty] | Security film (6 mils) | sqft | 15% | 10% | 25% | [30 empty] | Panel "MCB4b" | lot | 15% | 10% | 25% | 5-way back mounting frame | set/s | 15% | 10% | 25% | ½" Ø EMT elbow | pc/s | 15% | 10% | 25% | [22 empty] | a.) Security film shall be 6 mils (0.006 inches) thick nominally, clear and shall look seamless upon installation. b.) Contractor shall examine and clean the glass surface from dust before installation. c.) Contractor shall notify DBP if there are defects/imperfections on the glass surface. d.) The film shall be installed according to the manufacturer's instruction. e.) Refer to schedule of glass panels at architectural plans. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Application: For use with krone module b.) Modules, quantity: 5-way c.) Panel Mounting: Flush d.) Panel Style: Straight e.) Material Type: High-impact, Flame retardant
[36 empty] | Security film (8 mils) | sqft | 15% | 10% | 25% | [30 empty] | Panel "MCB4c" | lot | 15% | 10% | 25% | Private Automatic Branch Exchange (PABX) | lot | 15% | 10% | 25% | ½" Ø EMT coupling and connector (compression type) | set/s | 15% | 10% | 25% | [22 empty] | a.) Security film shall be 8 mils (0.008 inches) thick nominally, clear and shall look seamless upon installation. b.) Contractor shall examine and clean the glass surface from dust before installation. c.) Contractor shall notify DBP if there are defects/imperfections on the glass surface. d.) The film shall be installed according to the manufacturer's instruction. e.) Refer to schedule of glass panels at architectural plans. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility with the system.
[36 empty] | Frosted film | sqft | 15% | 10% | 25% | [30 empty] | Panel "LP4" | lot | 15% | 10% | 25% | Testing and commissioning | lot | 15% | 10% | 25% | Junction box with cover (PVC) | set/s | 15% | 10% | 25% | [22 empty] | a.) Security film shall be made of PVC film with frosted design and shall look seamless upon installation. b.) Contractor shall examine and clean the glass surface from dust before installation. c.) Contractor shall notify DBP if there are defects/imperfections on the glass surface. d.) The film shall be installed according to the manufacturer's instruction. e.) Refer to schedule of glass panels at architectural plans and/or schedule of doors at DBP standard booklet. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[36 empty] | Tinted film | sqft | 15% | 10% | 25% | [30 empty] | Panel "LP4a" | lot | 15% | 10% | 25% | Duplex data port outlet (Pop-up) | set/s | 15% | 10% | 25% | Utility box (PVC) | set/s | 15% | 10% | 25% | [42 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[36 empty] | Relocation of door/s | lot | 15% | 10% | 25% | [30 empty] | Panel "LP4b" | lot | 15% | 10% | 25% | Duplex voice port outlet (Pop-up) | set/s | 15% | 10% | 25% | [47 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[36 empty] | Replacement of broken window glass | lot | 15% | 10% | 25% | [30 empty] | Panel "LP4c" | lot | 15% | 10% | 25% | Junction box with cover (PVC) | set/s | 15% | 10% | 25% | [47 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[36 empty] | Interior frameless glass door (single) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PP4" | lot | 15% | 10% | 25% | Utility box (PVC) | set/s | 15% | 10% | 25% | [27 empty] | a.) Door size: 900mm width x 2100mm length/height b.) Shall be made of 12mm thick clear tempered glass panel. c.) Frosted glass sticker shall be provided d.) Refer to schedule of doors at DBP standard booklet. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[36 empty] | Curtain wall system | sqm | 15% | 10% | 25% | [30 empty] | Panel "PP4a" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[36 empty] | Hollow metal door with louver (single) | set/s | 15% | 10% | 25% | [30 empty] | Panel "PP4b" | lot | 15% | 10% | 25% | [32 empty] | a.) Opening size: 800mm width x 2100mm length/height b.) Door thickness: 50mm c.) Door material: GA 16 galvanized sheets on both sides cladded with stainless sheets; framing per manufacturer's standard; d.) Door jamb: 4" thk GA 16 single rabbet metal jamb with stainless steel finish e.) Stainless louver shall be included g.) Refer to schedule of doors at DBP standard booklet. | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[36 empty] | Main glass door sticker | lot | 15% | 10% | 25% | [30 empty] | Panel "PP4c" | lot | 15% | 10% | 25% | [32 empty] | a.) Decals shall be computer cut-out and wet type installation b.) Refer to decals details on booklet | [19 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "PPAC4" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "PPAC4a" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "PPAC4b" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "PPAC4c" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "PPUPS4" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "PPUPS4a" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "PPUPS4b" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "PPUPS4c" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "MDP" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA3R gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panelboard - NEMA1 (see drawings) | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panelboard - NEMA3R (see drawings) | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "TX-PRIMARY" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "TX-SECONDARY" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA1 gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) Circuit breakers shall be properly grounded and protected from mechanical damage. g.) Contractor to install all necessary accessories required to operate the device h.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | Panel "PGH" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA3R gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) No fabrication and installation shall be done without DBP’s proper approval
[71 empty] | Panel "ATS" | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide NEMA3R gauge #16 GI sheet powder coated (color:gray) fully bolted enclosure with twist lock and key b.) Contractor to install all necessary accessories; nameplate, mounting accessories, grounding terminals, and tin plated cooper busbars with insulators c.) Contractor must submit sample/s, technical specification and shop drawing for DBP’s approval before fabrication and installation d.) No fabrication and installation shall be done without DBP’s proper approval e.) 'Programmable digital controller: Min. LCD display features: Voltage (V), Frequency (Hz), Auto/Manual; Min. Keypad Controls: Power On/Off, Operation Manual/Automatic
[71 empty] | PABX phenolic backboard | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall verify cabinet dimensions. b.) Contractor shall provide galvanized phenolic board backing.
[71 empty] | TTC backboard | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall verify cabinet dimensions. b.) Contractor shall provide galvanized phenolic board backing.
[71 empty] | Timer switches phenolic backboard | lot | 15% | 10% | 25% | [52 empty] | a.) Contractor shall verify cabinet dimensions. b.) Contractor shall provide galvanized phenolic board backing.
[71 empty] | Panelboard tagging (laminated) | lot | 15% | 10% | 25% | [52 empty] | Contractor shall provide laminated tagging on all panelboards, ATS/MTS and ECBs.
[71 empty] | 20AT/100AF, 1-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 25AT/100AF, 1-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 30AT/100AF, 1-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 40AT/100AF, 1-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 50AT/100AF, 1-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 60AT/100AF, 1-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 75AT/100AF, 1-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 80AT/100AF, 1-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 100AT/100AF, 1-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 200AT/250AF, 1-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 20AT/100AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 20AT/100AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 30AT/100AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 30AT/100AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 40AT/100AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 40AT/100AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 50AT/100AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 50AT/100AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 100AT/100AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 125AT/250AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 160AT/250AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 200AT/250AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 225AT/250AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 250AT/250AF, 2-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 20AT/100AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 25AT/100AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 30AT/100AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 40AT/100AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 50AT/100AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 60AT/100AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 75AT/100AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 80AT/100AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 100AT/100AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 125AT/250AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 160AT/250AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 200AT/250AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 225AT/250AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 250AT/250AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 320AT/400AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 350AT/400AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 400AT/400AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 500AT/630AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 630AT/630AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 800AT/800AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 1000AT/1000AF, 3-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 160AT/250AF, 4-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 200AT/250AF, 4-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 800AT/800AF, 4-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 1000AT/1000AF, 4-Pole MCCB, with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
[71 empty] | 50A, 2-Pole (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | 100A, 2-Pole (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | 100A, 3-Pole (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | 160A, 3-pole, (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | 200A, 3-pole, (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | 315A, 3-pole, (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | 400A, 3-pole, (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | 500A, 3-pole, (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | 630A, 3-pole, (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | 125AT, 4-pole, (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | 160AT, 4-pole, (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | 200AT, 4-pole, (ATS) | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install Automatic Transfer Switch (ATS): With rating and number of poles based on the description; Setting and Configuration for adjustable timers for transfer time, and voltage/frequency thresholds; Voltage and Frequency sensing for control logic; Built-in of testing and monitoring features including alarms, emergency manual override, LED indicators, test buttons, and digital user interface display. b.) Contractor shall ensure Automatic Transfer Switch (ATS) is compatible with generator and utility power with safety features for overcurrent protection, short circuit protection, mechanical and electrical interlocking c.) Contractor to install all necessary accessories to operate the ATS. d.) Contractor must provide toggle handle fixed mounted 60Hz Automatic Transfer Switch (ATS); and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. e.) ATS shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 f.) ATS shall be properly grounded and protected from mechanical damage.
[71 empty] | Digital electric meter (Single phase), with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install round type, 60Hz, 3Φ, 200 ampere class, 4/5 jaws fixed mounted digital electric meter in #16 GI sheet powder coated NEMA-3R enclosure ; rated voltage shall be dependent on electrical system of the plan. b.) Digital electric meters shall be ERC certified. c.) Contractor to install necessary accessories.
[71 empty] | Digital electric meter (Three phase), with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install round type, 60Hz, 3Φ, 200 ampere class, 4/5 jaws fixed mounted digital electric meter in #16 GI sheet powder coated NEMA-3R enclosure ; rated voltage shall be dependent on electrical system of the plan. b.) Digital electric meters shall be ERC certified. c.) Contractor to install necessary accessories.
[71 empty] | 3-75/5A class 0.5-1, 400V (current transformer), with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install ring type current transformer enclosed in NEMA-3R gauge #16 b.) Contractor shall ensure its compatible with the system. c.) Ring type current transformer shall be IEC certified d.) Contractor to install all necessarry accessories to complete the system.
[71 empty] | 3-100/5A class 0.5-1, 400V (current transformer), with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install ring type current transformer enclosed in NEMA-3R gauge #16 b.) Contractor shall ensure its compatible with the system. c.) Ring type current transformer shall be IEC certified d.) Contractor to install all necessarry accessories to complete the system.
[71 empty] | 3-150/5A class 0.5-1, 400V (current transformer), with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install ring type current transformer enclosed in NEMA-3R gauge #16 b.) Contractor shall ensure its compatible with the system. c.) Ring type current transformer shall be IEC certified d.) Contractor to install all necessarry accessories to complete the system.
[71 empty] | 3-200/5A class 0.5-1, 400V (current transformer), with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install ring type current transformer enclosed in NEMA-3R gauge #16 b.) Contractor shall ensure its compatible with the system. c.) Ring type current transformer shall be IEC certified d.) Contractor to install all necessarry accessories to complete the system.
[71 empty] | 3-250/5A class 0.5-1, 400V (current transformer), with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install ring type current transformer enclosed in NEMA-3R gauge #16 b.) Contractor shall ensure its compatible with the system. c.) Ring type current transformer shall be IEC certified d.) Contractor to install all necessarry accessories to complete the system.
[71 empty] | 3-300/5A class 0.5-1, 400V (current transformer), with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install ring type current transformer enclosed in NEMA-3R gauge #16 b.) Contractor shall ensure its compatible with the system. c.) Ring type current transformer shall be IEC certified d.) Contractor to install all necessarry accessories to complete the system.
[71 empty] | 3-400/5A class 0.5-1, 400V (current transformer), with NEMA enclosure | set/s | 15% | 10% | 25% | [52 empty] | a.) Contractor shall provide and install ring type current transformer enclosed in NEMA-3R gauge #16 b.) Contractor shall ensure its compatible with the system. c.) Ring type current transformer shall be IEC certified d.) Contractor to install all necessarry accessories to complete the system.
[71 empty] | 5.5mm² 3C Royal cord wire | m | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 3.5mm² THHN stranded wire (150m/roll) | roll/s | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 5.5mm² THHN stranded wire (150m/roll) | roll/s | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 8.0mm² THHN stranded wire (150m/roll) | roll/s | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 14mm² THHN stranded wire | m | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 22mm² THHN stranded wire | m | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 30mm² THHN stranded wire | m | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 38mm² THHN stranded wire | m | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 50mm² THHN stranded wire | m | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 60mm² THHN stranded wire | m | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 80mm² THHN stranded wire | m | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 100mm² THHN stranded wire | m | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 125mm² THHN stranded wire | m | 15% | 10% | 25% | [52 empty] | 600 Volt grade wire shall be copper, hard drawn, annealed and shall be of 910% conductivity
[71 empty] | 20mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 25mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 32mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 40mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 50mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 63mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 75mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 80mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 90mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 110mmØ PVC pipe (3m/pc), with adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 32mmØ PVC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 40mmØ PVC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 50mmØ PVC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 63mmØ PVC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 75mmØ PVC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 80mmØ PVC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 90mmØ PVC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 110mmØ PVC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 20mm dia PVC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 25mm dia PVC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 32mm dia PVC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 40mm dia PVC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 50mm dia PVC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 63mm dia PVC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 75mm dia PVC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 80mm dia PVC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 90mm dia PVC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 110mm dia PVC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 20mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 25mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 32mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 40mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 50mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 63mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 75mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 80mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 90mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 110mm dia PVC adapter and locknut | set/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 25mm dia PVC end bell | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 32mm dia PVC end bell | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 40mm dia PVC end bell | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 50mm dia PVC end bell | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 63mm dia PVC end bell | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 75mm dia PVC end bell | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 80mm dia PVC end bell | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 90mm dia PVC end bell | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 110mm dia PVC end bell | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 12.7mm dia IMC conduit (3m/pc) with locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | Conduits shall be hot-dip galvanized steel material and length shall be 3.05m in length with coupling on one end.
[71 empty] | 19.0mm dia IMC conduit (3m/pc) with locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | Conduits shall be hot-dip galvanized steel material and length shall be 3.05m in length with coupling on one end.
[71 empty] | 25.4mm dia IMC conduit (3m/pc) with locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | Conduits shall be hot-dip galvanized steel material and length shall be 3.05m in length with coupling on one end.
[71 empty] | 31.7mm dia IMC conduit (3m/pc) with locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | Conduits shall be hot-dip galvanized steel material and length shall be 3.05m in length with coupling on one end.
[71 empty] | 38.1mm dia IMC conduit (3m/pc) with locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | Conduits shall be hot-dip galvanized steel material and length shall be 3.05m in length with coupling on one end.
[71 empty] | 50.8mm dia IMC conduit (3m/pc) with locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | Conduits shall be hot-dip galvanized steel material and length shall be 3.05m in length with coupling on one end.
[71 empty] | 63.5mm dia IMC conduit (3m/pc) with locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | Conduits shall be hot-dip galvanized steel material and length shall be 3.05m in length with coupling on one end.
[71 empty] | 76.2mm dia IMC conduit (3m/pc) with locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | Conduits shall be hot-dip galvanized steel material and length shall be 3.05m in length with coupling on one end.
[71 empty] | 88.9mm dia IMC conduit (3m/pc) with locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | Conduits shall be hot-dip galvanized steel material and length shall be 3.05m in length with coupling on one end.
[71 empty] | 101.6mm dia IMC conduit (3m/pc) with locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | Conduits shall be hot-dip galvanized steel material and length shall be 3.05m in length with coupling on one end.
[71 empty] | 12.7mm dia IMC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 19.0mm dia IMC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 25.4mm dia IMC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 31.7mm dia IMC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 38.1mm dia IMC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 50.8mm dia IMC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 63.5mm dia IMC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 76.2mm dia IMC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 88.9mm dia IMC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 101.6mm dia IMC elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 12.7mm dia IMC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 19.0mm dia IMC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 25.4mm dia IMC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 31.7mm dia IMC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 38.1mm dia IMC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 50.8mm dia IMC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 63.5mm dia IMC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 76.2mm dia IMC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 88.9mm dia IMC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 101.6mm dia IMC coupling | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 12.7mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 19.0mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 25.4mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 31.7mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 38.1mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 50.8mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 63.5mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 76.2mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 88.9mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 101.6mm dia IMC locknut and bushing | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 12.7mm dia EMT conduit | pc/s | 15% | 10% | 25% | [52 empty] | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end.
[71 empty] | 19.0mm dia EMT conduit | pc/s | 15% | 10% | 25% | [52 empty] | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end.
[71 empty] | 25.4mm dia EMT conduit | pc/s | 15% | 10% | 25% | [52 empty] | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end.
[71 empty] | 31.7mm dia EMT conduit | pc/s | 15% | 10% | 25% | [52 empty] | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end.
[71 empty] | 38.1mm dia EMT conduit | pc/s | 15% | 10% | 25% | [52 empty] | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end.
[71 empty] | 50.8mm dia EMT conduit | pc/s | 15% | 10% | 25% | [52 empty] | a.) Conduits shall be hot-dip galvanized steel material. b.) Standard product length shall be 3.05m and has coupling on one end.
[71 empty] | 12.7mm dia EMT elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 19.0mm dia EMT elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 25.4mm dia EMT elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 31.7mm dia EMT elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 38.1mm dia EMT elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 50.8mm dia EMT elbow | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 12.7mm dia EMT coupling and connector (set screw type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 19.0mm dia EMT coupling and connector (set screw type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 25.4mm dia EMT coupling and connector (set screw type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 31.7mm dia EMT coupling and connector (set screw type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 38.1mm dia EMT coupling and connector (set screw type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 50.8mm dia EMT coupling and connector (set screw type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 12.7mm dia EMT coupling and connector (compression type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 19.0mm dia EMT coupling and connector (compression type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 25.4mm dia EMT coupling and connector (compression type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 31.7mm dia EMT coupling and connector (compression type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 38.1mm dia EMT coupling and connector (compression type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 50.8mm dia EMT coupling and connector (compression type) | set/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 50mm dia liquid tight flexible metal conduit (20m/roll) | roll/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 50mm dia straight connector | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 50mm dia angle connector | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 40mm dia liquid tight flexible metal conduit (25m/roll) | roll/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 40mm dia straight connector | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 40mm dia angle connector | pc/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 20mmØ flexible metal conduit (50m/roll) | roll/s | 15% | 10% | 25% | [52 empty] | shall be hot-dip galvanized steel material.
[71 empty] | 20mmØ flexible PVC pipe (50m/roll) | roll/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 20mmØ straight connector | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 20mmØ angle connector | pc/s | 15% | 10% | 25% | [52 empty] | shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness.
[71 empty] | 50mmØ service entrance cap | pc/s | 15% | 10% | 25% | [52 empty] | Contractor shall provide and install die-cast aluminum service entrance cap and installation accessories
[71 empty] | 40mmØ service entrance cap | pc/s | 15% | 10% | 25% | [52 empty] | Contractor shall provide and install die-cast aluminum service entrance cap and installation accessories
[71 empty] | 63mmØ service entrance cap | pc/s | 15% | 10% | 25% | [52 empty] | Contractor shall provide and install die-cast aluminum service entrance cap and installation accessories
[71 empty] | 110mmØ service entrance cap | pc/s | 15% | 10% | 25% | [52 empty] | Contractor shall provide and install die-cast aluminum service entrance cap and installation accessories
[71 empty] | Grounding rod (3/4" x 3m) | pc/s | 15% | 10% | 25% | [52 empty] | shall be 3/4" diameter x 3m long copper ground rod.
[71 empty] | Grounding clamp | pc/s | 15% | 10% | 25% | [52 empty] | shall be copper-plated.
[71 empty] | Hanger and support | lot | 15% | 10% | 25% | [52 empty] | Hanger rod shall be 6mm dia. bar with expansion shield and bolted on underslab.
[71 empty] | Consumables (tape, PVC cement, & accessories) | lot | 0% | 10% | 10% | [52 empty] | All necessary consumables to complete the electrical works shall be included.
[71 empty] | Junction box with cover (ga#16) | set/s | 15% | 10% | 25% | [52 empty] | a.) Junction box dimensions: 4" x 4" (GA#16) b.) Junction box deep type with cover and shall be made of galvanized iron.
[71 empty] | Utility box (ga#16) | set/s | 15% | 10% | 25% | [52 empty] | a.) Utility box dimensions: 4" x 2" (GA#16) b.) Utility box deep type and shall be made of galvanized iron.
[71 empty] | Pullbox (ga#16) | set/s | 15% | 10% | 25% | [52 empty] | a.) Pullbox dimensions: 24"x 24" x 16" (GA#16) b.) Pullbox material shall be made of galvanized iron.
[71 empty] | Wire gutter | pc/s | 15% | 10% | 25% | [52 empty] | Wire gutter shall be made of galvanized iron.
[71 empty] | 1-gang switch with plate (16A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 1 gang switch with plate cover b.) Color: white c.) Rating: 16A d.) Voltage: 220-250V e.) Material: polycarbonate
[71 empty] | 2-gang switch with plate (16A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 2 gang switch with plate cover b.) Color: white c.) Rating: 16A d.) Voltage: 220-250V e.) Material: polycarbonate
[71 empty] | 3-gang switch with plate (16A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 3 gang switch with plate cover b.) Color: white c.) Rating: 16A d.) Voltage: 220-250V e.) Material: polycarbonate
[71 empty] | 1-gang 3-way switch with plate (16A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 1 gang 3-way switch with plate cover b.) Color: white c.) Rating: 16A d.) Voltage: 220-250V e.) Material: polycarbonate
[71 empty] | 2-gang 3-way switch with plate (16A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 2 gang 3-way switch with plate cover b.) Color: white c.) Rating: 16A d.) Voltage: 220-250V e.) Material: polycarbonate
[71 empty] | 3-gang 3-way switch with plate (16A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 3 gang 3-way switch with plate cover b.) Color: white c.) Rating: 16A d.) Voltage: 220-250V e.) Material: polycarbonate
[71 empty] | 16A Duplex universal outlet with ground (wall mounted) | set/s | 15% | 10% | 25% | [52 empty] | a.) Outlet type: duplex universal outlet with ground b.) Color: white c.) Mounting type: wall mounted d.) Rating: 16A e.) Voltage: 220-250V f.) Material: polycarbonate
[71 empty] | 16A Duplex universal outlet with ground (wall mounted, weatherproof type) | set/s | 15% | 10% | 25% | [52 empty] | a.) Outlet type: duplex universal outlet with ground weather proof type b.) Color: white c.) Mounting type: wall mounted d.) Rating: 16A e.) Voltage: 220-250V f.) Material: polycarbonate
[71 empty] | 16A Pop-up convenience outlet (floor mounted) | set/s | 15% | 10% | 25% | [52 empty] | a.) Outlet type: Pop-up conveneince outlet b.) Color: white c.) Mounting type: floor mounted d.) Rating: 16A e.) Voltage: 220-250V
[71 empty] | 3prong twistlock outlet with plug (20A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 3-prong twist lock outlet w/ cover b.) 3-prong plug specifications: c.) Color: beige d.) Mounting type: wall mounted e.) Rating: 20A f.) Voltage: 220-250V
[71 empty] | 3prong twistlock outlet with plug (30A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 3-prong twist lock outlet w/ cover b.) 3-prong plug specifications: c.) Color: beige d.) Mounting type: wall mounted e.) Rating: 30A f.) Voltage: 220-250V
[71 empty] | 3prong twistlock outlet with plug (40A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 3-prong twist lock outlet w/ cover b.) 3-prong plug specifications: c.) Color: beige d.) Mounting type: wall mounted e.) Rating: 40A f.) Voltage: 220-250V
[71 empty] | 3prong twistlock outlet with plug (50A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 3-prong twist lock outlet w/ cover b.) 3-prong plug specifications: c.) Color: beige d.) Mounting type: wall mounted e.) Rating: 50A f.) Voltage: 220-250V
[71 empty] | 4prong twistlock outlet with plug (40A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 4-prong twist lock outlet w/ cover b.) 4-prong plug specifications: c.) Color: beige d.) Mounting type: wall mounted e.) Rating: 40A f.) Voltage: 220-250V
[71 empty] | 4prong twistlock outlet with plug (50A) | set/s | 15% | 10% | 25% | [52 empty] | a.) Switch type: 4-prong twist lock outlet w/ cover b.) 4-prong plug specifications: c.) Color: beige d.) Mounting type: wall mounted e.) Rating: 50A f.) Voltage: 220-250V
[71 empty] | 24 hour timer switch | set/s | 15% | 10% | 25% | [52 empty] | a.) Mounting: wall mounted mechanical timer switch b.) Timer: 15 mins - 24 hour timing range (can be manually override). c.) Contractor shall ensure timer switch is compatible with signage, magnetic contactor, and electrical system.
[71 empty] | Magnetic contactor | set/s | 15% | 10% | 25% | [52 empty] | a. Contractor to provide and install magnetic contactor with min. of 9A contact rating and 3 poles contact configuration (3NO). b. Contractor shall ensure magnetic contactor is compatible with signage, timer switch, and electrical system.
[71 empty] | Steel enclosure for switchbank with lock and key | set/s | 15% | 10% | 25% | [52 empty] | a.) Galvanized sheet with lock b.) Fully bolted construction enclosure c.) Color: white d.) Fixed type
[71 empty] | 2-3W LED Emergency lamp with battery | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | LED exit sign with white acrylic housing | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | 1-8W 60cm T5 LED tube (warm white) | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | 1-16W 120cm T5 LED tube (warm white) | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | 2-16W 120cm T5 LED tube(daylight) w/ 60x120cm mirrorized fixture (recessed) | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | 2-16W 120cm T5 LED tube(daylight) w/ 60x120cm dustproof louver fixture (recessed) | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | 2-16W 120cm T5 LED tube(coolwhite) w/ 60x120cm dustproof louver fixture (recessed) | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | 1-15W E-27 LED bulb(daylight) w/ 6"Ø E-27 downlight fixture (recessed) | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | 1-15W E-27 LED bulb(warm white) w/ 6"Ø E-27 downlight fixture (recessed) | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | 1-15W E-27 LED bulb(warm white) w/ 6"Ø E-27 downlight glass covered fixture (surface-mount) | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | 2-10W E-27 LED bulb(warm white) w/ E-27 socket bi-directional fixture (wall mounted) | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | 1-10W LED bulb (warm white) w/ weather proof stake lamp holder | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | LED strip lights | lot | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | Relocation and re-use of existing lighting fixtures | lot | 15% | 10% | 25%
[71 empty] | Mounting termination, testing and commissioning | lot | 15% | 10% | 25% | [52 empty] | Contractor holds responsibility for mounting termination, testing (megger test, full load test, load balancing test, etc.,), and commissioning to ensure that every component and system is operational
[71 empty] | Battery pack for lighting fixture | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | 1-8W 600mm T5 LED tube (4000-4500k) on 600mm covered fixture (surface mount) | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | Service entrance post | lot | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | Concrete manhole for feeder lines | lot | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | Application of permanent power inclusive of Distribution Transformer/s for the DBP total load requirement (Actual No/s. and ratings shall be based on the final recommendation Electric Cooperative), mounting accessories, and Primary & Secondary wiring | lot | 15% | 10% | 25% | [52 empty] | a.) The Contractor shall ensure the cooling class type; Oil immersed, self-cooled (non-PCB type). b.) Contractor to use mineral oil for insulation fluid and copper for winding with temperature rise of winding not to exceed 65°C. c.) Contractor to install all necessary standard mounting accessories, and shoulder transformer hauling to operate the system. d.) Contractor must refer to electrical plans for details. Notes: 1. Bill deposit care of DBP. 2. Items to be calibrated/tested by service provider prior to installation. 3. Contractor to submit proof of result/approval by service provider prior through submission of certification/transmittal or tempered-proof seal. 4. Contractor shall submit all documents and pay all fees.
[71 empty] | Transient Voltage Surge Suppressor (TVSS) with NEMA Enclosure | lot | 15% | 10% | 25% | [52 empty] | Shall be based on manufacturer standard
[71 empty] | Unitized Cabinet | lot | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
[71 empty] | Unitized Cabinet 2 (1000 x 1850 x 300) | lot | 15% | 10% | 25%
[71 empty] | Junction box with cover (PVC) | set/s | 15% | 10% | 25%
[71 empty] | Utility box (PVC) | set/s | 15% | 10% | 25%
[71 empty] | 1-15W LED tracklight (daylight) with 100cm black alluminum track bar | set/s | 15% | 10% | 25% | [52 empty] | Contractor must refer to electrical plans for location and specifications and to install all necessary accessories to complete system.
a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval
a.) Contractor shall provide and install toggle handle fixed mounted 60Hz circuit breaker; and rated service short-circuit breaking capacity shall be dependent on the computed short circuit current in the electrical plan; rated voltage shall be dependent on electrical system of the plan. b.) Circuit breakers shall comply with the following standards: - IEC 60898-1:2015 - ANSI/IEEE C37.20.1-2015 - UL 489 c.) Circuit breakers shall be properly grounded and protected from mechanical damage. d.) Contractor to install all necessary accessories required to operate the device e.) No fabrication and installation shall be done without DBP's proper approval

## BOQ-
SUPPLY, DELIVERY, INSTALLATION TESTING AND COMMISSIONING OF CCTV SURVEILLANCE SYSTEM FOR DBP DAET BRANCH
Project Name
J. P. RIZAL STREET, DAET, BICOL
Project Location
SCOPE OF WORKS / MATERIALS SPECIFICATIONS
The Contractor shall hold all obligations, duties, and responsibilities necessary to the successful completion of the contract assigned to or be undertaken, including all labor, materials, equipment and services, other incidentals, i.e. bonds and insurance, contractor’s all risk insurance (CARI); and furnishings thereof in accordance with the drawings, specifications and all addenda prepared by DBP.
BILL OF QUANTITIES
ITEM NO. | DESCRIPTION | SCOPE OF WORKS / SPECIFICATIONS | QTY. | UNIT | LABOR & MAT'LS | MARK-UP | PROFIT | TOTAL MARK-UP |  | VAT | TOTAL | TOTAL COST | UNIT COST
[5 empty] | DIRECT COST | OCM |  | % | VALUE |  | INDIRECT COST
1 | GENERAL REQUIREMENTS
1.1 | Construction health and safety program | a.) Wearing of ANSI standard PPEs, provision of safety signages and compliance to DOH, DOLE and LGU protocols shall be observed on the project site. b.) A bonafide Safety Officer shall always be present on site. | 1 | lot
1.2 | Mobilization and demobilization | - | 1 | lot
1.3 | Site maintenance
1.3.1 | Hauling/disposal | a.) All old materials, trash, debris, including hazardous waste (spills) shall be removed from the immediate work area as the work progresses. It shall be carefully piled up and/or properly seggregated in a appropriate container before disposal. b.) Weekly hauling is required. | 1 | lot
[11 empty] | Sub-total= | 0
2 | SITE CONDITIONS
2.1 | Dismantling works | a.) All dismantled items/materials shall be turned-over to Lessor b.) Refer to as-found/demolition plan | 1 | lot
[11 empty] | Sub-total= | 0
3 | CONCRETE | a.) Gravel shall be clean, washed, and graded “G-1” crushed stone aggregates conforming to ASTM C-33. b.) Sand shall be cleaned, washed and free from deleterious materials conforming to ASTM C-40. c.) Water shall be clean, clear and without acidic or salinic contents. d.) Cement shall be portland cement or approved equal conforming to ASTM C-150.
3.1 | Concrete members
3.2.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
4 | MASONRY
4.1. | Exterior masonry walls (including rebars and mortar fillers)
4.1.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
5 | METALS
5.1 | Metal fabrications | All fabricated metal components shall be painted with two (2) coats zinc dust zinc-oxide primer.
5.1.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
6 | WOODS PLASTICS AND COMPOSITES
6.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
7 | THERMAL AND MOISTURE PROTECTION
|  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
7 | DOORS AND WINDOWS
7.1 | Wooden doors (including door jamb)
7.1.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
8 | FINISHES
8.1 | Wall finishes
8.1.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
9 | SPECIALTIES
9.1 | Signages
9.1.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
10 | FURNISHINGS
10.1 | Office furnitures
10.1.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
11 | FIRE SUPPRESSION SYSTEM
11.1 | Fire extinguishing equipments
11.1.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
12 | PLUMBING
12.1 | Kitchen/toilet fixtures and accessories
12.1.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
13 | HVAC
13.1 | Packaged HVAC systems
13.1.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
14 | ELECTRICAL
14.1 | Application of Permanent Power
14.1.1 |  | - |  | - |  | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0 |  | #REF! | #REF!
15 | POWER GENERATING EQUIPMENT
15.1 | Generator
15.1.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
-
[11 empty] | Sub-total= | 0
16 | COMMUNICATIONS
16.1 | Network system
16.1.1 |  | - |  | - |  | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
3 | ELECTRONIC SAFETY AND SECURITY
3.1 | CCTV Surveillance System
3.1.1 | 9U CCTV Cabinet (wall mounted) | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system. | 1 | set/s
3.1.3 | 5MP CCTV camera (bullet type) | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system. | 2 | set/s
3.1.4 | 5MP CCTV camera (dome type) | a.) Contractor to refer to ECE plans for technical specfications and locations. b.) Contractor to install all necessary accessories to complete and operate the system. c.) Contractor to ensure compatibility & readiness of the system for central monitoring integration. d.) Contractor shall provide all manuals and must schedule and conduct orientation/training for the DBP branch personnel for the maintenance and upkeep of the installed CCTVs. e.) Contractor to provide and install all necessary accessories to complete the system. | 3 | set/s
3.2 | Wires and cables
3.2.1 | Cat5e UTP cable 4 pairs (305m/box) | a.) Cat5e UTP cable 4 pairs min. 100mbps receiving b.) Conductors: Solid bare copper conductors c.) Insulators: Polyolefin insulation d.) Jacket: Gray PVC jacket with rip cord | 1 | box/es
3.3 | Conduits and fittings
3.3.1 | 25.4mm dia EMT conduit (3m/pc) |  | 30 | pc/s
3.3.2 | 25.4mm dia EMT elbow |  | 40 | pc/s
3.3.3 | 25.4mm dia EMT coupling and connector (compression type) |  | 40 | set/s
3.3.4 | 25mmØ PVC pipe (3m/pc), with adapter and locknut | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness, compression and impact resistant, non-corrosive, weatherproof | 60 | set/s
3.3.5 | 20mmØ flexible PVC pipe (50m/roll) | Pipe shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness, compression and impact resistant, non-corrosive, weatherproof | 2 | roll/s
3.3.6 | 20mmØ straight connector | a.) Pullbox dimensions: 24"x 24" x 16" (GA#16) b.) Pullbox material shall be made of galvanized iron. | 20 | set/s | [9 empty] | 0 |  | 595
3.3.7 | 20mmØ angle connector | Angle connector shall be unplasticized Polyvinyl Chloride (uPVC), schedule 40 and uniform in thickness. | 20 | set/s | [9 empty] | 0 |  | 340 | 113.3333
3.4 | Boxes | [12 empty] | 0 |  | 425
3.4.1 | Pullbox (ga#16) | a.) Pullbox dimensions: 24"x 24" x 16" (GA#16) b.) Pullbox material shall be made of galvanized iron. | 1 | set/s | [9 empty] | 0 |  | 1.1148
3.4.2 | Junction box with cover (PVC) | 0 | 20 | set/s | [9 empty] | 0 |  | 1.3934
3.5 | Other accessories
3.5.1 | Hanger and support | Hanger rod shall be 6mm dia. bar with expansion shield and bolted on underslab. | 1 | lot
3.5.2 | Consumables (tape, tagging, PVC cement and accessories) | All necessary consumables to complete the electrical works shall be included. | 1 | lot
3.5.3 | Mounting termination, testing, commissioning and programming | Contractor holds responsibility for mounting termination, testing, commissioning and programming to ensure that every component and system is operational | 1 | lot
[11 empty] | Sub-total= | 0
18 | EARTHWORK
18.1 |  | - |  | - | 0 | 0 | 0 | - | - | - | - | - | -
[11 empty] | Sub-total= | 0
20 | EXTERIOR IMPROVEMENTS
|  |  |  | - |  | 0 | 0 | - | - | - | - | - | -
21 | HANDLING EQUIPMENT
|  |  |  | - |  | 0 | 0 | - | - | - | - | - | -
[11 empty] | Total= | 0
Prepared by: Reviewed by: | Prepared by: |  | Reviewed by:
ENGR. JUDE MATTHEW V. MERINO AM MICHAEL ANTOLIN F. CANCIO
PDO I, CFMD-PCMU Acting Head, PCMU
Prepared by: |  |  | Reviewed by: |  |  |  | Recommended by: |  |  |  | Aproved by:
ENGR. MAICO IOWIE B. MOLINA |  |  | ENGR. JESSIE E. DELGADO |  |  |  | SM. ERICK M. VALIDO |  |  |  | SAVP. ALBERTO SANTIAGO A. BERMEJO
JO- Technical Staff |  |  | Acting Head, PM HO, Luzon Team, PCMU-CFMD |  |  |  | OIC, Project & Contracts Management Unit |  |  |  | The OIC, Construction & Facilities Management Dept.
(per Sector Order No. 513 dated 20 August 2025